## Calculation
Starting conditions (Condition no 1) :
OK
pressure (absolute) | 1 | bar (absolute) | OK
Temperature (degr Celcius) | 40 | degr.Celcius | OK
Relative humidity % | 60 | % | OK
Saturated water vapor pressure | 0.072789 | bar
Vapor pressure | 0.043674 | bar
pressure dry air | 0.95633 | bar
density dry air | 1.0785 | kg/m3
specific volume dry air | 0.92721 | m3/kg
Water vapor content | 0.029298 | kg/kg(dry air)
Total mass dry air + vapor | 1.0293 | kg
density starting conditions | 1.1101 | kg/m3
specific volume at intake conditions | 0.90082 | m3/kg
Dew point temperature at pressure | 31.2538 | degr.Celcius
Local conditions (Condition no 2) :
OK
pressure (absolute) | 7 | bar (absolute) | OK
Temperature (degr Celcius) | 50 | degr. Celcius | OK
Relative humidity % | 100 | %
Saturated water vapor pressure | 0.12174 | bar
Vapor pressure | 0.12174 | bar
pressure dry air | 6.8783 | bar
density dry air | 7.5169 | kg/m3
specific volume dry air | 0.13303 | m3/kg
Water vapor content | 0.011009 | kg/kg(dry air)
Total mass dry air + vapor | 1.011 | kg
density local conditions | 7.5996 | kg/m3
Dew point temperature at pressure + condenstion | 50 | degr.Celcius
Dew point temperature at pressure - no condensation | 70.5345 | degr.Celcius
Condensated mass of water | 0.018289 | kg/kg(dry air)
Volume of transport intake air | 1200 | m3/hr
Conveyed material | 150 | tons/hr
Condensated water | 23.6697 | kg/hr
Bonded mass of cement | 99.8862 | kg/hr
| 0.066591 | %
OK
OK
OK
OK
RH-calculation from wet bulb temperature
pressure (absolute) | 1 | bar (absolute)
Ambient temperature (degr Celcius) | 40 | degr. Celcius
Wet bulb temperature | 32.5 | degr. Celcius
Psychometric difference | 7.5 | degr. Celcius
Relative humidity % | 59 | %
Saturated water vapor pressure tamb | 0.072789 | bar(absolute)
Vapor pressure | 0.042946 | bar(absolute)
Water vapor content | 0.028809 | kg/kg(dry air)
pressure dry air ambient | 0.95705 | bar(absolute)
density dry air | 1.0793 | kg/m3
specific volume dry air | 0.9265 | m3/kg
Dew point temperature at pressure | 30.9749 | degr. Celcius
Total mass dry air + vapor | 1.0288 | kg
density local conditions | 1.1104 | kg/m3
Note on C40: Remark: Volume of pneumatic conveying compressor or Volume in silo above cement
Note on C41: Remark: Capacity rate or mass of product

## Table
|  |  |  | Pressure | 1 | [9 empty] | Pressure |  |  |  | RH tamb | Pressure |  |  | Condition 1 | [5 empty] | Condition2 |  |  |  |  | Condition2 |  |  |  |  | RH
|  | saturated | saturated | relative humidity | 100% |  |  | saturated | saturated |  |  |  | saturated | saturated | relative humidity |  |  | saturated | saturated | relative humidity |  |  | saturated | sat dew point |  |  |  |  | saturated | sat dew point |  |  |  | saturated | sat dew point |  |  |  | saturated | sat dew point
| temperature | water vapour pressure | water vapour pressure |  | Saturared water |  | temperature | water vapour pressure | water vapour pressure |  |  | temperature | water vapour pressure | water vapour pressure |  |  | temperature | water vapour pressure | water vapour pressure |  |  | temperature | water vapour pressure | water vapor pressure |  |  |  | temperature | water vapour pressure | water vapor pressure |  |  | temperature | water vapour pressure | water vapor pressure |  |  | temperature | water vapour pressure | water vapor pressure
|  | inch Hg | bar |  | content |  |  | inch Hg | bar |  |  |  | inch Hg | bar |  |  |  | inch Hg | bar |  |  |  | bar | [5 empty] | bar |  |  |  |  | bar |  |  |  |  | bar
| -55 | 0.015 | 1.9737e-05 | 0 | 1.2277e-05 |  | -55 | 0.015 | 1.9737e-05 | 0 |  | -55 | 0.015 | 1.9737e-05 | 0 |  | -55 | 0.015 | 1.9737e-05 | 0 |  | -55 | 1.9737e-05 | 0.044983 | 0 |  |  | -55 | 1.9737e-05 | 0.12174 | 0 |  | -55 | 1.9737e-05 | 0.31488 | 0 |  | -55 | 1.9737e-05 | 0.044267 | 0
| -50 | 0.029 | 3.8158e-05 | 0 | 2.3735e-05 |  | -50 | 0.029 | 3.8158e-05 | 0 |  | -50 | 0.029 | 3.8158e-05 | 0 |  | -50 | 0.029 | 3.8158e-05 | 0 |  | -50 | 3.8158e-05 | 0.044983 | 0 |  |  | -50 | 3.8158e-05 | 0.12174 | 0 |  | -50 | 3.8158e-05 | 0.31488 | 0 |  | -50 | 3.8158e-05 | 0.044267 | 0
| -45 | 0.052 | 6.8421e-05 | 0 | 4.2561e-05 |  | -45 | 0.052 | 6.8421e-05 | 0 |  | -45 | 0.052 | 6.8421e-05 | 0 |  | -45 | 0.052 | 6.8421e-05 | 0 |  | -45 | 6.8421e-05 | 0.044983 | 0 |  |  | -45 | 6.8421e-05 | 0.12174 | 0 |  | -45 | 6.8421e-05 | 0.31488 | 0 |  | -45 | 6.8421e-05 | 0.044267 | 0
| -40 | 0.093 | 0.00012237 | 0 | 7.6122e-05 |  | -40 | 0.093 | 0.00012237 | 0 |  | -40 | 0.093 | 0.00012237 | 0 |  | -40 | 0.093 | 0.00012237 | 0 |  | -40 | 0.00012237 | 0.044983 | 0 |  |  | -40 | 0.00012237 | 0.12174 | 0 |  | -40 | 0.00012237 | 0.31488 | 0 |  | -40 | 0.00012237 | 0.044267 | 0
| -38 | 0.119 | 0.00015658 | 0 | 9.7407e-05 |  | -38 | 0.119 | 0.00015658 | 0 |  | -38 | 0.119 | 0.00015658 | 0 |  | -38 | 0.119 | 0.00015658 | 0 |  | -38 | 0.00015658 | 0.044983 | 0 |  |  | -38 | 0.00015658 | 0.12174 | 0 |  | -38 | 0.00015658 | 0.31488 | 0 |  | -38 | 0.00015658 | 0.044267 | 0
| -36 | 0.15 | 0.00019737 | 0 | 0.00012279 |  | -36 | 0.15 | 0.00019737 | 0 |  | -36 | 0.15 | 0.00019737 | 0 |  | -36 | 0.15 | 0.00019737 | 0 |  | -36 | 0.00019737 | 0.044983 | 0 |  |  | -36 | 0.00019737 | 0.12174 | 0 |  | -36 | 0.00019737 | 0.31488 | 0 |  | -36 | 0.00019737 | 0.044267 | 0
| -34 | 0.185 | 0.00024342 | 0 | 0.00015144 |  | -34 | 0.185 | 0.00024342 | 0 |  | -34 | 0.185 | 0.00024342 | 0 |  | -34 | 0.185 | 0.00024342 | 0 |  | -34 | 0.00024342 | 0.044983 | 0 |  |  | -34 | 0.00024342 | 0.12174 | 0 |  | -34 | 0.00024342 | 0.31488 | 0 |  | -34 | 0.00024342 | 0.044267 | 0
| -32 | 0.227 | 0.00029868 | 0 | 0.00018584 |  | -32 | 0.227 | 0.00029868 | 0 |  | -32 | 0.227 | 0.00029868 | 0 |  | -32 | 0.227 | 0.00029868 | 0 |  | -32 | 0.00029868 | 0.044983 | 0 |  |  | -32 | 0.00029868 | 0.12174 | 0 |  | -32 | 0.00029868 | 0.31488 | 0 |  | -32 | 0.00029868 | 0.044267 | 0
| -30 | 0.28 | 0.00036842 | 0 | 0.00022924 |  | -30 | 0.28 | 0.00036842 | 0 |  | -30 | 0.28 | 0.00036842 | 0 |  | -30 | 0.28 | 0.00036842 | 0 |  | -30 | 0.00036842 | 0.044983 | 0 |  |  | -30 | 0.00036842 | 0.12174 | 0 |  | -30 | 0.00036842 | 0.31488 | 0 |  | -30 | 0.00036842 | 0.044267 | 0
| -28 | 0.345 | 0.00045395 | 0 | 0.00028248 |  | -28 | 0.345 | 0.00045395 | 0 |  | -28 | 0.345 | 0.00045395 | 0 |  | -28 | 0.345 | 0.00045395 | 0 |  | -28 | 0.00045395 | 0.044983 | 0 |  |  | -28 | 0.00045395 | 0.12174 | 0 |  | -28 | 0.00045395 | 0.31488 | 0 |  | -28 | 0.00045395 | 0.044267 | 0
| -26 | 0.425 | 0.00055921 | 0 | 0.00034802 |  | -26 | 0.425 | 0.00055921 | 0 |  | -26 | 0.425 | 0.00055921 | 0 |  | -26 | 0.425 | 0.00055921 | 0 |  | -26 | 0.00055921 | 0.044983 | 0 |  |  | -26 | 0.00055921 | 0.12174 | 0 |  | -26 | 0.00055921 | 0.31488 | 0 |  | -26 | 0.00055921 | 0.044267 | 0
| -24 | 0.521 | 0.00068553 | 0 | 0.00042669 |  | -24 | 0.521 | 0.00068553 | 0 |  | -24 | 0.521 | 0.00068553 | 0 |  | -24 | 0.521 | 0.00068553 | 0 |  | -24 | 0.00068553 | 0.044983 | 0 |  |  | -24 | 0.00068553 | 0.12174 | 0 |  | -24 | 0.00068553 | 0.31488 | 0 |  | -24 | 0.00068553 | 0.044267 | 0
| -22 | 0.636 | 0.00083684 | 0 | 0.00052095 |  | -22 | 0.636 | 0.00083684 | 0 |  | -22 | 0.636 | 0.00083684 | 0 |  | -22 | 0.636 | 0.00083684 | 0 |  | -22 | 0.00083684 | 0.044983 | 0 |  |  | -22 | 0.00083684 | 0.12174 | 0 |  | -22 | 0.00083684 | 0.31488 | 0 |  | -22 | 0.00083684 | 0.044267 | 0
| -20 | 0.772 | 0.0010158 | 0 | 0.00063246 |  | -20 | 0.772 | 0.0010158 | 0 |  | -20 | 0.772 | 0.0010158 | 0 |  | -20 | 0.772 | 0.0010158 | 0 |  | -20 | 0.0010158 | 0.044983 | 0 |  |  | -20 | 0.0010158 | 0.12174 | 0 |  | -20 | 0.0010158 | 0.31488 | 0 |  | -20 | 0.0010158 | 0.044267 | 0
| -19 | 0.85 | 0.0011184 | 0 | 0.00069644 |  | -19 | 0.85 | 0.0011184 | 0 |  | -19 | 0.85 | 0.0011184 | 0 |  | -19 | 0.85 | 0.0011184 | 0 |  | -19 | 0.0011184 | 0.044983 | 0 |  |  | -19 | 0.0011184 | 0.12174 | 0 |  | -19 | 0.0011184 | 0.31488 | 0 |  | -19 | 0.0011184 | 0.044267 | 0
| -18 | 0.935 | 0.0012303 | 0 | 0.00076617 |  | -18 | 0.935 | 0.0012303 | 0 |  | -18 | 0.935 | 0.0012303 | 0 |  | -18 | 0.935 | 0.0012303 | 0 |  | -18 | 0.0012303 | 0.044983 | 0 |  |  | -18 | 0.0012303 | 0.12174 | 0 |  | -18 | 0.0012303 | 0.31488 | 0 |  | -18 | 0.0012303 | 0.044267 | 0
| -17 | 1.027 | 0.0013513 | 0 | 0.00084166 |  | -17 | 1.027 | 0.0013513 | 0 |  | -17 | 1.027 | 0.0013513 | 0 |  | -17 | 1.027 | 0.0013513 | 0 |  | -17 | 0.0013513 | 0.044983 | 0 |  |  | -17 | 0.0013513 | 0.12174 | 0 |  | -17 | 0.0013513 | 0.31488 | 0 |  | -17 | 0.0013513 | 0.044267 | 0
| -16 | 1.128 | 0.0014842 | 0 | 0.00092455 |  | -16 | 1.128 | 0.0014842 | 0 |  | -16 | 1.128 | 0.0014842 | 0 |  | -16 | 1.128 | 0.0014842 | 0 |  | -16 | 0.0014842 | 0.044983 | 0 |  |  | -16 | 0.0014842 | 0.12174 | 0 |  | -16 | 0.0014842 | 0.31488 | 0 |  | -16 | 0.0014842 | 0.044267 | 0
| -15 | 1.238 | 0.0016289 | 0 | 0.0010149 |  | -15 | 1.238 | 0.0016289 | 0 |  | -15 | 1.238 | 0.0016289 | 0 |  | -15 | 1.238 | 0.0016289 | 0 |  | -15 | 0.0016289 | 0.044983 | 0 |  |  | -15 | 0.0016289 | 0.12174 | 0 |  | -15 | 0.0016289 | 0.31488 | 0 |  | -15 | 0.0016289 | 0.044267 | 0
| -14 | 1.357 | 0.0017855 | 0 | 0.0011126 |  | -14 | 1.357 | 0.0017855 | 0 |  | -14 | 1.357 | 0.0017855 | 0 |  | -14 | 1.357 | 0.0017855 | 0 |  | -14 | 0.0017855 | 0.044983 | 0 |  |  | -14 | 0.0017855 | 0.12174 | 0 |  | -14 | 0.0017855 | 0.31488 | 0 |  | -14 | 0.0017855 | 0.044267 | 0
| -13 | 1.486 | 0.0019553 | 0 | 0.0012186 |  | -13 | 1.486 | 0.0019553 | 0 |  | -13 | 1.486 | 0.0019553 | 0 |  | -13 | 1.486 | 0.0019553 | 0 |  | -13 | 0.0019553 | 0.044983 | 0 |  |  | -13 | 0.0019553 | 0.12174 | 0 |  | -13 | 0.0019553 | 0.31488 | 0 |  | -13 | 0.0019553 | 0.044267 | 0
| -12 | 1.627 | 0.0021408 | 0 | 0.0013344 |  | -12 | 1.627 | 0.0021408 | 0 |  | -12 | 1.627 | 0.0021408 | 0 |  | -12 | 1.627 | 0.0021408 | 0 |  | -12 | 0.0021408 | 0.044983 | 0 |  |  | -12 | 0.0021408 | 0.12174 | 0 |  | -12 | 0.0021408 | 0.31488 | 0 |  | -12 | 0.0021408 | 0.044267 | 0
| -11 | 1.78 | 0.0023421 | 0 | 0.0014602 |  | -11 | 1.78 | 0.0023421 | 0 |  | -11 | 1.78 | 0.0023421 | 0 |  | -11 | 1.78 | 0.0023421 | 0 |  | -11 | 0.0023421 | 0.044983 | 0 |  |  | -11 | 0.0023421 | 0.12174 | 0 |  | -11 | 0.0023421 | 0.31488 | 0 |  | -11 | 0.0023421 | 0.044267 | 0
| -10 | 1.946 | 0.0025605 | 0 | 0.0015967 |  | -10 | 1.946 | 0.0025605 | 0 |  | -10 | 1.946 | 0.0025605 | 0 |  | -10 | 1.946 | 0.0025605 | 0 |  | -10 | 0.0025605 | 0.044983 | 0 |  |  | -10 | 0.0025605 | 0.12174 | 0 |  | -10 | 0.0025605 | 0.31488 | 0 |  | -10 | 0.0025605 | 0.044267 | 0
| -9 | 2.125 | 0.0027961 | 0 | 0.001744 |  | -9 | 2.125 | 0.0027961 | 0 |  | -9 | 2.125 | 0.0027961 | 0 |  | -9 | 2.125 | 0.0027961 | 0 |  | -9 | 0.0027961 | 0.044983 | 0 |  |  | -9 | 0.0027961 | 0.12174 | 0 |  | -9 | 0.0027961 | 0.31488 | 0 |  | -9 | 0.0027961 | 0.044267 | 0
| -8 | 2.321 | 0.0030539 | 0 | 0.0019054 |  | -8 | 2.321 | 0.0030539 | 0 |  | -8 | 2.321 | 0.0030539 | 0 |  | -8 | 2.321 | 0.0030539 | 0 |  | -8 | 0.0030539 | 0.044983 | 0 |  |  | -8 | 0.0030539 | 0.12174 | 0 |  | -8 | 0.0030539 | 0.31488 | 0 |  | -8 | 0.0030539 | 0.044267 | 0
| -7 | 2.532 | 0.0033316 | 0 | 0.0020792 |  | -7 | 2.532 | 0.0033316 | 0 |  | -7 | 2.532 | 0.0033316 | 0 |  | -7 | 2.532 | 0.0033316 | 0 |  | -7 | 0.0033316 | 0.044983 | 0 |  |  | -7 | 0.0033316 | 0.12174 | 0 |  | -7 | 0.0033316 | 0.31488 | 0 |  | -7 | 0.0033316 | 0.044267 | 0
| -6 | 2.761 | 0.0036329 | 0 | 0.0022679 |  | -6 | 2.761 | 0.0036329 | 0 |  | -6 | 2.761 | 0.0036329 | 0 |  | -6 | 2.761 | 0.0036329 | 0 |  | -6 | 0.0036329 | 0.044983 | 0 |  |  | -6 | 0.0036329 | 0.12174 | 0 |  | -6 | 0.0036329 | 0.31488 | 0 |  | -6 | 0.0036329 | 0.044267 | 0
| -5 | 3.008 | 0.0039579 | 0 | 0.0024716 |  | -5 | 3.008 | 0.0039579 | 0 |  | -5 | 3.008 | 0.0039579 | 0 |  | -5 | 3.008 | 0.0039579 | 0 |  | -5 | 0.0039579 | 0.044983 | 0 |  |  | -5 | 0.0039579 | 0.12174 | 0 |  | -5 | 0.0039579 | 0.31488 | 0 |  | -5 | 0.0039579 | 0.044267 | 0
| -4 | 3.275 | 0.0043092 | 0 | 0.0026919 |  | -4 | 3.275 | 0.0043092 | 0 |  | -4 | 3.275 | 0.0043092 | 0 |  | -4 | 3.275 | 0.0043092 | 0 |  | -4 | 0.0043092 | 0.044983 | 0 |  |  | -4 | 0.0043092 | 0.12174 | 0 |  | -4 | 0.0043092 | 0.31488 | 0 |  | -4 | 0.0043092 | 0.044267 | 0
| -3 | 3.566 | 0.0046921 | 0 | 0.0029322 |  | -3 | 3.566 | 0.0046921 | 0 |  | -3 | 3.566 | 0.0046921 | 0 |  | -3 | 3.566 | 0.0046921 | 0 |  | -3 | 0.0046921 | 0.044983 | 0 |  |  | -3 | 0.0046921 | 0.12174 | 0 |  | -3 | 0.0046921 | 0.31488 | 0 |  | -3 | 0.0046921 | 0.044267 | 0
| -2 | 3.879 | 0.0051039 | 0 | 0.0031909 |  | -2 | 3.879 | 0.0051039 | 0 |  | -2 | 3.879 | 0.0051039 | 0 |  | -2 | 3.879 | 0.0051039 | 0 |  | -2 | 0.0051039 | 0.044983 | 0 |  |  | -2 | 0.0051039 | 0.12174 | 0 |  | -2 | 0.0051039 | 0.31488 | 0 |  | -2 | 0.0051039 | 0.044267 | 0
| -1 | 4.216 | 0.0055474 | 0 | 0.0034697 |  | -1 | 4.216 | 0.0055474 | 0 |  | -1 | 4.216 | 0.0055474 | 0 |  | -1 | 4.216 | 0.0055474 | 0 |  | -1 | 0.0055474 | 0.044983 | 0 |  |  | -1 | 0.0055474 | 0.12174 | 0 |  | -1 | 0.0055474 | 0.31488 | 0 |  | -1 | 0.0055474 | 0.044267 | 0
| 0 | 4.581 | 0.0060276 | 0 | 0.0037719 |  | 0 | 4.581 | 0.0060276 | 0 |  | 0 | 4.581 | 0.0060276 | 0 |  | 0 | 4.581 | 0.0060276 | 0 |  | 0 | 0.0060276 | 0.044983 | 0 |  |  | 0 | 0.0060276 | 0.12174 | 0 |  | 0 | 0.0060276 | 0.31488 | 0 |  | 0 | 0.0060276 | 0.044267 | 0
| 1 | 4.924 | 0.0064789 | 0 | 0.0040562 |  | 1 | 4.924 | 0.0064789 | 0 |  | 1 | 4.924 | 0.0064789 | 0 |  | 1 | 4.924 | 0.0064789 | 0 |  | 1 | 0.0064789 | 0.044983 | 0 |  |  | 1 | 0.0064789 | 0.12174 | 0 |  | 1 | 0.0064789 | 0.31488 | 0 |  | 1 | 0.0064789 | 0.044267 | 0
| 2 | 5.291 | 0.0069618 | 0 | 0.0043606 |  | 2 | 5.291 | 0.0069618 | 0 |  | 2 | 5.291 | 0.0069618 | 0 |  | 2 | 5.291 | 0.0069618 | 0 |  | 2 | 0.0069618 | 0.044983 | 0 |  |  | 2 | 0.0069618 | 0.12174 | 0 |  | 2 | 0.0069618 | 0.31488 | 0 |  | 2 | 0.0069618 | 0.044267 | 0
| 3 | 5.681 | 0.007475 | 0 | 0.0046845 |  | 3 | 5.681 | 0.007475 | 0 |  | 3 | 5.681 | 0.007475 | 0 |  | 3 | 5.681 | 0.007475 | 0 |  | 3 | 0.007475 | 0.044983 | 0 |  |  | 3 | 0.007475 | 0.12174 | 0 |  | 3 | 0.007475 | 0.31488 | 0 |  | 3 | 0.007475 | 0.044267 | 0
| 4 | 6.097 | 0.0080224 | 0 | 0.0050303 |  | 4 | 6.097 | 0.0080224 | 0 |  | 4 | 6.097 | 0.0080224 | 0 |  | 4 | 6.097 | 0.0080224 | 0 |  | 4 | 0.0080224 | 0.044983 | 0 |  |  | 4 | 0.0080224 | 0.12174 | 0 |  | 4 | 0.0080224 | 0.31488 | 0 |  | 4 | 0.0080224 | 0.044267 | 0
| 5 | 6.539 | 0.0086039 | 0 | 0.0053981 |  | 5 | 6.539 | 0.0086039 | 0 |  | 5 | 6.539 | 0.0086039 | 0 |  | 5 | 6.539 | 0.0086039 | 0 |  | 5 | 0.0086039 | 0.044983 | 0 |  |  | 5 | 0.0086039 | 0.12174 | 0 |  | 5 | 0.0086039 | 0.31488 | 0 |  | 5 | 0.0086039 | 0.044267 | 0
| 7 | 7.51 | 0.0098816 | 0 | 0.0062077 |  | 7 | 7.51 | 0.0098816 | 0 |  | 7 | 7.51 | 0.0098816 | 0 |  | 7 | 7.51 | 0.0098816 | 0 |  | 7 | 0.0098816 | 0.044983 | 0 |  |  | 7 | 0.0098816 | 0.12174 | 0 |  | 7 | 0.0098816 | 0.31488 | 0 |  | 7 | 0.0098816 | 0.044267 | 0
| 8 | 8.041 | 0.01058 | 0 | 0.0066513 |  | 8 | 8.041 | 0.01058 | 0 |  | 8 | 8.041 | 0.01058 | 0 |  | 8 | 8.041 | 0.01058 | 0 |  | 8 | 0.01058 | 0.044983 | 0 |  |  | 8 | 0.01058 | 0.12174 | 0 |  | 8 | 0.01058 | 0.31488 | 0 |  | 8 | 0.01058 | 0.044267 | 0
| 9 | 8.606 | 0.011324 | 0 | 0.007124 |  | 9 | 8.606 | 0.011324 | 0 |  | 9 | 8.606 | 0.011324 | 0 |  | 9 | 8.606 | 0.011324 | 0 |  | 9 | 0.011324 | 0.044983 | 0 |  |  | 9 | 0.011324 | 0.12174 | 0 |  | 9 | 0.011324 | 0.31488 | 0 |  | 9 | 0.011324 | 0.044267 | 0
| 10 | 9.204 | 0.012111 | 0 | 0.0076251 |  | 10 | 9.204 | 0.012111 | 0 |  | 10 | 9.204 | 0.012111 | 0 |  | 10 | 9.204 | 0.012111 | 0 |  | 10 | 0.012111 | 0.044983 | 0 |  |  | 10 | 0.012111 | 0.12174 | 0 |  | 10 | 0.012111 | 0.31488 | 0 |  | 10 | 0.012111 | 0.044267 | 0
| 11 | 9.839 | 0.012946 | 0 | 0.0081581 |  | 11 | 9.839 | 0.012946 | 0 |  | 11 | 9.839 | 0.012946 | 0 |  | 11 | 9.839 | 0.012946 | 0 |  | 11 | 0.012946 | 0.044983 | 0 |  |  | 11 | 0.012946 | 0.12174 | 0 |  | 11 | 0.012946 | 0.31488 | 0 |  | 11 | 0.012946 | 0.044267 | 0
| 12 | 10.512 | 0.013832 | 0 | 0.0087239 |  | 12 | 10.512 | 0.013832 | 0 |  | 12 | 10.512 | 0.013832 | 0 |  | 12 | 10.512 | 0.013832 | 0 |  | 12 | 0.013832 | 0.044983 | 0 |  |  | 12 | 0.013832 | 0.12174 | 0 |  | 12 | 0.013832 | 0.31488 | 0 |  | 12 | 0.013832 | 0.044267 | 0
| 13 | 11.226 | 0.014771 | 0 | 0.0093253 |  | 13 | 11.226 | 0.014771 | 0 |  | 13 | 11.226 | 0.014771 | 0 |  | 13 | 11.226 | 0.014771 | 0 |  | 13 | 0.014771 | 0.044983 | 0 |  |  | 13 | 0.014771 | 0.12174 | 0 |  | 13 | 0.014771 | 0.31488 | 0 |  | 13 | 0.014771 | 0.044267 | 0
| 14 | 11.982 | 0.015766 | 0 | 0.0099634 |  | 14 | 11.982 | 0.015766 | 0 |  | 14 | 11.982 | 0.015766 | 0 |  | 14 | 11.982 | 0.015766 | 0 |  | 14 | 0.015766 | 0.044983 | 0 |  |  | 14 | 0.015766 | 0.12174 | 0 |  | 14 | 0.015766 | 0.31488 | 0 |  | 14 | 0.015766 | 0.044267 | 0
| 15 | 12.781 | 0.016817 | 0 | 0.010639 |  | 15 | 12.781 | 0.016817 | 0 |  | 15 | 12.781 | 0.016817 | 0 |  | 15 | 12.781 | 0.016817 | 0 |  | 15 | 0.016817 | 0.044983 | 0 |  |  | 15 | 0.016817 | 0.12174 | 0 |  | 15 | 0.016817 | 0.31488 | 0 |  | 15 | 0.016817 | 0.044267 | 0
| 16 | 13.628 | 0.017932 | 0 | 0.011357 |  | 16 | 13.628 | 0.017932 | 0 |  | 16 | 13.628 | 0.017932 | 0 |  | 16 | 13.628 | 0.017932 | 0 |  | 16 | 0.017932 | 0.044983 | 0 |  |  | 16 | 0.017932 | 0.12174 | 0 |  | 16 | 0.017932 | 0.31488 | 0 |  | 16 | 0.017932 | 0.044267 | 0
| 17 | 14.524 | 0.019111 | 0 | 0.012118 |  | 17 | 14.524 | 0.019111 | 0 |  | 17 | 14.524 | 0.019111 | 0 |  | 17 | 14.524 | 0.019111 | 0 |  | 17 | 0.019111 | 0.044983 | 0 |  |  | 17 | 0.019111 | 0.12174 | 0 |  | 17 | 0.019111 | 0.31488 | 0 |  | 17 | 0.019111 | 0.044267 | 0
| 18 | 15.47 | 0.020355 | 0 | 0.012924 |  | 18 | 15.47 | 0.020355 | 0 |  | 18 | 15.47 | 0.020355 | 0 |  | 18 | 15.47 | 0.020355 | 0 |  | 18 | 0.020355 | 0.044983 | 0 |  |  | 18 | 0.020355 | 0.12174 | 0 |  | 18 | 0.020355 | 0.31488 | 0 |  | 18 | 0.020355 | 0.044267 | 0
| 19 | 16.47 | 0.021671 | 0 | 0.013778 |  | 19 | 16.47 | 0.021671 | 0 |  | 19 | 16.47 | 0.021671 | 0 |  | 19 | 16.47 | 0.021671 | 0 |  | 19 | 0.021671 | 0.044983 | 0 |  |  | 19 | 0.021671 | 0.12174 | 0 |  | 19 | 0.021671 | 0.31488 | 0 |  | 19 | 0.021671 | 0.044267 | 0
| 20 | 17.53 | 0.023066 | 0 | 0.014686 |  | 20 | 17.53 | 0.023066 | 0 |  | 20 | 17.53 | 0.023066 | 0 |  | 20 | 17.53 | 0.023066 | 0 |  | 20 | 0.023066 | 0.044983 | 0 |  |  | 20 | 0.023066 | 0.12174 | 0 |  | 20 | 0.023066 | 0.31488 | 0 |  | 20 | 0.023066 | 0.044267 | 0
| 21 | 18.64 | 0.024526 | 0 | 0.015639 |  | 21 | 18.64 | 0.024526 | 0 |  | 21 | 18.64 | 0.024526 | 0 |  | 21 | 18.64 | 0.024526 | 0 |  | 21 | 0.024526 | 0.044983 | 0 |  |  | 21 | 0.024526 | 0.12174 | 0 |  | 21 | 0.024526 | 0.31488 | 0 |  | 21 | 0.024526 | 0.044267 | 0
| 22 | 19.82 | 0.026079 | 0 | 0.016655 |  | 22 | 19.82 | 0.026079 | 0 |  | 22 | 19.82 | 0.026079 | 0 |  | 22 | 19.82 | 0.026079 | 0 |  | 22 | 0.026079 | 0.044983 | 0 |  |  | 22 | 0.026079 | 0.12174 | 0 |  | 22 | 0.026079 | 0.31488 | 0 |  | 22 | 0.026079 | 0.044267 | 0
| 23 | 21.06 | 0.027711 | 0 | 0.017727 |  | 23 | 21.06 | 0.027711 | 0 |  | 23 | 21.06 | 0.027711 | 0 |  | 23 | 21.06 | 0.027711 | 0 |  | 23 | 0.027711 | 0.044983 | 0 |  |  | 23 | 0.027711 | 0.12174 | 0 |  | 23 | 0.027711 | 0.31488 | 0 |  | 23 | 0.027711 | 0.044267 | 0
| 24 | 22.37 | 0.029434 | 0 | 0.018863 |  | 24 | 22.37 | 0.029434 | 0 |  | 24 | 22.37 | 0.029434 | 0 |  | 24 | 22.37 | 0.029434 | 0 |  | 24 | 0.029434 | 0.044983 | 0 |  |  | 24 | 0.029434 | 0.12174 | 0 |  | 24 | 0.029434 | 0.31488 | 0 |  | 24 | 0.029434 | 0.044267 | 0
| 25 | 23.75 | 0.03125 | 0 | 0.020065 |  | 25 | 23.75 | 0.03125 | 0 |  | 25 | 23.75 | 0.03125 | 0 |  | 25 | 23.75 | 0.03125 | 0 |  | 25 | 0.03125 | 0.044983 | 0 |  |  | 25 | 0.03125 | 0.12174 | 0 |  | 25 | 0.03125 | 0.31488 | 0 |  | 25 | 0.03125 | 0.044267 | 0
| 26 | 25.2 | 0.033158 | 0 | 0.021332 |  | 26 | 25.2 | 0.033158 | 0 |  | 26 | 25.2 | 0.033158 | 0 |  | 26 | 25.2 | 0.033158 | 0 |  | 26 | 0.033158 | 0.044983 | 0 |  |  | 26 | 0.033158 | 0.12174 | 0 |  | 26 | 0.033158 | 0.31488 | 0 |  | 26 | 0.033158 | 0.044267 | 0
| 27 | 26.37 | 0.034697 | 0 | 0.022358 |  | 27 | 26.37 | 0.034697 | 0 |  | 27 | 26.37 | 0.034697 | 0 |  | 27 | 26.37 | 0.034697 | 0 |  | 27 | 0.034697 | 0.044983 | 0 |  |  | 27 | 0.034697 | 0.12174 | 0 |  | 27 | 0.034697 | 0.31488 | 0 |  | 27 | 0.034697 | 0.044267 | 0
| 28 | 28.34 | 0.037289 | 0 | 0.024092 |  | 28 | 28.34 | 0.037289 | 0 |  | 28 | 28.34 | 0.037289 | 0 |  | 28 | 28.34 | 0.037289 | 0 |  | 28 | 0.037289 | 0.044983 | 0 |  |  | 28 | 0.037289 | 0.12174 | 0 |  | 28 | 0.037289 | 0.31488 | 0 |  | 28 | 0.037289 | 0.044267 | 0
| 29 | 30.03 | 0.039513 | 0 | 0.025588 |  | 29 | 30.03 | 0.039513 | 0 |  | 29 | 30.03 | 0.039513 | 0 |  | 29 | 30.03 | 0.039513 | 0 |  | 29 | 0.039513 | 0.044983 | 0 |  |  | 29 | 0.039513 | 0.12174 | 0 |  | 29 | 0.039513 | 0.31488 | 0 |  | 29 | 0.039513 | 0.044267 | 0
| 30 | 31.81 | 0.041855 | 0 | 0.027171 |  | 30 | 31.81 | 0.041855 | 0 |  | 30 | 31.81 | 0.041855 | 0 |  | 30 | 31.81 | 0.041855 | 0 |  | 30 | 0.041855 | 0.044983 | 0 |  |  | 30 | 0.041855 | 0.12174 | 0 |  | 30 | 0.041855 | 0.31488 | 0 |  | 30 | 0.041855 | 0.044267 | 30.9749
| 31 | 33.69 | 0.044329 | 0 | 0.028852 |  | 31 | 33.69 | 0.044329 | 0 |  | 31 | 33.69 | 0.044329 | 0 |  | 31 | 33.69 | 0.044329 | 0 |  | 31 | 0.044329 | 0.044983 | 31.2538 |  |  | 31 | 0.044329 | 0.12174 | 0 |  | 31 | 0.044329 | 0.31488 | 0 |  | 31 | 0.044329 | 0.044267 | 0
| 32 | 35.65 | 0.046908 | 0 | 0.030613 |  | 32 | 35.65 | 0.046908 | 0 |  | 32 | 35.65 | 0.046908 | 0.04827 |  | 32 | 35.65 | 0.046908 | 0 |  | 32 | 0.046908 | 0.044983 | 0 |  |  | 32 | 0.046908 | 0.12174 | 0 |  | 32 | 0.046908 | 0.31488 | 0 |  | 32 | 0.046908 | 0.044267 | 0
| 33 | 37.72 | 0.049632 | 0 | 0.032483 |  | 33 | 37.72 | 0.049632 | 0 |  | 33 | 37.72 | 0.049632 | 0 |  | 33 | 37.72 | 0.049632 | 0 |  | 33 | 0.049632 | 0.044983 | 0 |  |  | 33 | 0.049632 | 0.12174 | 0 |  | 33 | 0.049632 | 0.31488 | 0 |  | 33 | 0.049632 | 0.044267 | 0
| 34 | 39.89 | 0.052487 | 0 | 0.034455 |  | 34 | 39.89 | 0.052487 | 0 |  | 34 | 39.89 | 0.052487 | 0 |  | 34 | 39.89 | 0.052487 | 0 |  | 34 | 0.052487 | 0.044983 | 0 |  |  | 34 | 0.052487 | 0.12174 | 0 |  | 34 | 0.052487 | 0.31488 | 0 |  | 34 | 0.052487 | 0.044267 | 0
| 35 | 42.17 | 0.055487 | 0 | 0.03654 |  | 35 | 42.17 | 0.055487 | 0 |  | 35 | 42.17 | 0.055487 | 0 |  | 35 | 42.17 | 0.055487 | 0 |  | 35 | 0.055487 | 0.044983 | 0 |  |  | 35 | 0.055487 | 0.12174 | 0 |  | 35 | 0.055487 | 0.31488 | 0 |  | 35 | 0.055487 | 0.044267 | 0
| 36 | 44.55 | 0.058618 | 0 | 0.038731 |  | 36 | 44.55 | 0.058618 | 0 |  | 36 | 44.55 | 0.058618 | 0 |  | 36 | 44.55 | 0.058618 | 0 |  | 36 | 0.058618 | 0.044983 | 0 |  |  | 36 | 0.058618 | 0.12174 | 0 |  | 36 | 0.058618 | 0.31488 | 0 |  | 36 | 0.058618 | 0.044267 | 0
| 37 | 47.06 | 0.061921 | 0 | 0.041057 |  | 37 | 47.06 | 0.061921 | 0 |  | 37 | 47.06 | 0.061921 | 0 |  | 37 | 47.06 | 0.061921 | 0 |  | 37 | 0.061921 | 0.044983 | 0 |  |  | 37 | 0.061921 | 0.12174 | 0 |  | 37 | 0.061921 | 0.31488 | 0 |  | 37 | 0.061921 | 0.044267 | 0
| 38 | 49.69 | 0.065382 | 0 | 0.043512 |  | 38 | 49.69 | 0.065382 | 0 |  | 38 | 49.69 | 0.065382 | 0 |  | 38 | 49.69 | 0.065382 | 0 |  | 38 | 0.065382 | 0.044983 | 0 |  |  | 38 | 0.065382 | 0.12174 | 0 |  | 38 | 0.065382 | 0.31488 | 0 |  | 38 | 0.065382 | 0.044267 | 0
| 39 | 52.44 | 0.069 | 0 | 0.046099 |  | 39 | 52.44 | 0.069 | 0 |  | 39 | 52.44 | 0.069 | 0 |  | 39 | 52.44 | 0.069 | 0 |  | 39 | 0.069 | 0.044983 | 0 |  |  | 39 | 0.069 | 0.12174 | 0 |  | 39 | 0.069 | 0.31488 | 0 |  | 39 | 0.069 | 0.044267 | 0
| 40 | 55.32 | 0.072789 | 0.072789 | 0.048829 |  | 40 | 55.32 | 0.072789 | 0 |  | 40 | 55.32 | 0.072789 | 0 |  | 40 | 55.32 | 0.072789 | 0.072789 |  | 40 | 0.072789 | 0.044983 | 0 |  |  | 40 | 0.072789 | 0.12174 | 0 |  | 40 | 0.072789 | 0.31488 | 0 |  | 40 | 0.072789 | 0.044267 | 0
| 41 | 58.33 | 0.07675 | 0 | 0.051707 |  | 41 | 58.33 | 0.07675 | 0 |  | 41 | 58.33 | 0.07675 | 0 |  | 41 | 58.33 | 0.07675 | 0 |  | 41 | 0.07675 | 0.044983 | 0 |  |  | 41 | 0.07675 | 0.12174 | 0 |  | 41 | 0.07675 | 0.31488 | 0 |  | 41 | 0.07675 | 0.044267 | 0
| 42 | 61.49 | 0.080908 | 0 | 0.054755 |  | 42 | 61.49 | 0.080908 | 0 |  | 42 | 61.49 | 0.080908 | 0 |  | 42 | 61.49 | 0.080908 | 0 |  | 42 | 0.080908 | 0.044983 | 0 |  |  | 42 | 0.080908 | 0.12174 | 0 |  | 42 | 0.080908 | 0.31488 | 0 |  | 42 | 0.080908 | 0.044267 | 0
| 43 | 64.8 | 0.085263 | 0 | 0.057977 |  | 43 | 64.8 | 0.085263 | 0 |  | 43 | 64.8 | 0.085263 | 0 |  | 43 | 64.8 | 0.085263 | 0 |  | 43 | 0.085263 | 0.044983 | 0 |  |  | 43 | 0.085263 | 0.12174 | 0 |  | 43 | 0.085263 | 0.31488 | 0 |  | 43 | 0.085263 | 0.044267 | 0
| 44 | 68.25 | 0.089803 | 0 | 0.061368 |  | 44 | 68.25 | 0.089803 | 0 |  | 44 | 68.25 | 0.089803 | 0 |  | 44 | 68.25 | 0.089803 | 0 |  | 44 | 0.089803 | 0.044983 | 0 |  |  | 44 | 0.089803 | 0.12174 | 0 |  | 44 | 0.089803 | 0.31488 | 0 |  | 44 | 0.089803 | 0.044267 | 0
| 45 | 71.87 | 0.094566 | 0 | 0.064963 |  | 45 | 71.87 | 0.094566 | 0 |  | 45 | 71.87 | 0.094566 | 0 |  | 45 | 71.87 | 0.094566 | 0 |  | 45 | 0.094566 | 0.044983 | 0 |  |  | 45 | 0.094566 | 0.12174 | 0 |  | 45 | 0.094566 | 0.31488 | 0 |  | 45 | 0.094566 | 0.044267 | 0
| 46 | 75.65 | 0.099539 | 0 | 0.068758 |  | 46 | 75.65 | 0.099539 | 0 |  | 46 | 75.65 | 0.099539 | 0 |  | 46 | 75.65 | 0.099539 | 0 |  | 46 | 0.099539 | 0.044983 | 0 |  |  | 46 | 0.099539 | 0.12174 | 0 |  | 46 | 0.099539 | 0.31488 | 0 |  | 46 | 0.099539 | 0.044267 | 0
| 47 | 79.6 | 0.10474 | 0 | 0.072768 |  | 47 | 79.6 | 0.10474 | 0 |  | 47 | 79.6 | 0.10474 | 0 |  | 47 | 79.6 | 0.10474 | 0 |  | 47 | 0.10474 | 0.044983 | 0 |  |  | 47 | 0.10474 | 0.12174 | 0 |  | 47 | 0.10474 | 0.31488 | 0 |  | 47 | 0.10474 | 0.044267 | 0
| 48 | 83.72 | 0.11016 | 0 | 0.077 |  | 48 | 83.72 | 0.11016 | 0 |  | 48 | 83.72 | 0.11016 | 0 |  | 48 | 83.72 | 0.11016 | 0 |  | 48 | 0.11016 | 0.044983 | 0 |  |  | 48 | 0.11016 | 0.12174 | 0 |  | 48 | 0.11016 | 0.31488 | 0 |  | 48 | 0.11016 | 0.044267 | 0
| 49 | 88.03 | 0.11583 | 0 | 0.081484 |  | 49 | 88.03 | 0.11583 | 0 |  | 49 | 88.03 | 0.11583 | 0 |  | 49 | 88.03 | 0.11583 | 0 |  | 49 | 0.11583 | 0.044983 | 0 |  |  | 49 | 0.11583 | 0.12174 | 0 |  | 49 | 0.11583 | 0.31488 | 0 |  | 49 | 0.11583 | 0.044267 | 0
| 50 | 92.52 | 0.12174 | 0 | 0.086216 |  | 50 | 92.52 | 0.12174 | 0.12174 |  | 50 | 92.52 | 0.12174 | 0 |  | 50 | 92.52 | 0.12174 | 0 |  | 50 | 0.12174 | 0.044983 | 0 |  |  | 50 | 0.12174 | 0.12174 | 50 |  | 50 | 0.12174 | 0.31488 | 0 |  | 50 | 0.12174 | 0.044267 | 0
| 52 | 102.11 | 0.13436 | 0 | 0.09654 |  | 52 | 102.11 | 0.13436 | 0 |  | 52 | 102.11 | 0.13436 | 0 |  | 52 | 102.11 | 0.13436 | 0 |  | 52 | 0.13436 | 0.044983 | 0 |  |  | 52 | 0.13436 | 0.12174 | 0 |  | 52 | 0.13436 | 0.31488 | 0 |  | 52 | 0.13436 | 0.044267 | 0
| 54 | 112.53 | 0.14807 | 0 | 0.1081 |  | 54 | 112.53 | 0.14807 | 0 |  | 54 | 112.53 | 0.14807 | 0 |  | 54 | 112.53 | 0.14807 | 0 |  | 54 | 0.14807 | 0.044983 | 0 |  |  | 54 | 0.14807 | 0.12174 | 0 |  | 54 | 0.14807 | 0.31488 | 0 |  | 54 | 0.14807 | 0.044267 | 0
| 56 | 123.83 | 0.16293 | 0 | 0.12107 |  | 56 | 123.83 | 0.16293 | 0 |  | 56 | 123.83 | 0.16293 | 0 |  | 56 | 123.83 | 0.16293 | 0 |  | 56 | 0.16293 | 0.044983 | 0 |  |  | 56 | 0.16293 | 0.12174 | 0 |  | 56 | 0.16293 | 0.31488 | 0 |  | 56 | 0.16293 | 0.044267 | 0
| 58 | 136.11 | 0.17909 | 0 | 0.1357 |  | 58 | 136.11 | 0.17909 | 0 |  | 58 | 136.11 | 0.17909 | 0 |  | 58 | 136.11 | 0.17909 | 0 |  | 58 | 0.17909 | 0.044983 | 0 |  |  | 58 | 0.17909 | 0.12174 | 0 |  | 58 | 0.17909 | 0.31488 | 0 |  | 58 | 0.17909 | 0.044267 | 0
| 60 | 149.39 | 0.19657 | 0 | 0.15218 |  | 60 | 149.39 | 0.19657 | 0 |  | 60 | 149.39 | 0.19657 | 0 |  | 60 | 149.39 | 0.19657 | 0 |  | 60 | 0.19657 | 0.044983 | 0 |  |  | 60 | 0.19657 | 0.12174 | 0 |  | 60 | 0.19657 | 0.31488 | 0 |  | 60 | 0.19657 | 0.044267 | 0
| 62 | 163.8 | 0.21553 | 0 | 0.17089 |  | 62 | 163.8 | 0.21553 | 0 |  | 62 | 163.8 | 0.21553 | 0 |  | 62 | 163.8 | 0.21553 | 0 |  | 62 | 0.21553 | 0.044983 | 0 |  |  | 62 | 0.21553 | 0.12174 | 0 |  | 62 | 0.21553 | 0.31488 | 0 |  | 62 | 0.21553 | 0.044267 | 0
| 64 | 179.3 | 0.23592 | 0 | 0.19205 |  | 64 | 179.3 | 0.23592 | 0 |  | 64 | 179.3 | 0.23592 | 0 |  | 64 | 179.3 | 0.23592 | 0 |  | 64 | 0.23592 | 0.044983 | 0 |  |  | 64 | 0.23592 | 0.12174 | 0 |  | 64 | 0.23592 | 0.31488 | 0 |  | 64 | 0.23592 | 0.044267 | 0
| 66 | 196.1 | 0.25803 | 0 | 0.2163 |  | 66 | 196.1 | 0.25803 | 0 |  | 66 | 196.1 | 0.25803 | 0 |  | 66 | 196.1 | 0.25803 | 0 |  | 66 | 0.25803 | 0.044983 | 0 |  |  | 66 | 0.25803 | 0.12174 | 0 |  | 66 | 0.25803 | 0.31488 | 0 |  | 66 | 0.25803 | 0.044267 | 0
| 68 | 214.2 | 0.28184 | 0 | 0.2441 |  | 68 | 214.2 | 0.28184 | 0 |  | 68 | 214.2 | 0.28184 | 0 |  | 68 | 214.2 | 0.28184 | 0 |  | 68 | 0.28184 | 0.044983 | 0 |  |  | 68 | 0.28184 | 0.12174 | 0 |  | 68 | 0.28184 | 0.31488 | 0 |  | 68 | 0.28184 | 0.044267 | 0
| 70 | 233.7 | 0.3075 | 0 | 0.27619 |  | 70 | 233.7 | 0.3075 | 0 |  | 70 | 233.7 | 0.3075 | 0 |  | 70 | 233.7 | 0.3075 | 0 |  | 70 | 0.3075 | 0.044983 | 0 |  |  | 70 | 0.3075 | 0.12174 | 0 |  | 70 | 0.3075 | 0.31488 | 70.5345 |  | 70 | 0.3075 | 0.044267 | 0
| 72 | 254.7 | 0.33513 | 0 | 0.31352 |  | 72 | 254.7 | 0.33513 | 0 |  | 72 | 254.7 | 0.33513 | 0 |  | 72 | 254.7 | 0.33513 | 0 |  | 72 | 0.33513 | 0.044983 | 0 |  |  | 72 | 0.33513 | 0.12174 | 0 |  | 72 | 0.33513 | 0.31488 | 0 |  | 72 | 0.33513 | 0.044267 | 0
| 74 | 277.2 | 0.36474 | 0 | 0.35712 |  | 74 | 277.2 | 0.36474 | 0 |  | 74 | 277.2 | 0.36474 | 0 |  | 74 | 277.2 | 0.36474 | 0 |  | 74 | 0.36474 | 0.044983 | 0 |  |  | 74 | 0.36474 | 0.12174 | 0 |  | 74 | 0.36474 | 0.31488 | 0 |  | 74 | 0.36474 | 0.044267 | 0
| 76 | 301.4 | 0.39658 | 0 | 0.40879 |  | 76 | 301.4 | 0.39658 | 0 |  | 76 | 301.4 | 0.39658 | 0 |  | 76 | 301.4 | 0.39658 | 0 |  | 76 | 0.39658 | 0.044983 | 0 |  |  | 76 | 0.39658 | 0.12174 | 0 |  | 76 | 0.39658 | 0.31488 | 0 |  | 76 | 0.39658 | 0.044267 | 0
| 78 | 327.4 | 0.43079 | 0 | 0.47074 |  | 78 | 327.4 | 0.43079 | 0 |  | 78 | 327.4 | 0.43079 | 0 |  | 78 | 327.4 | 0.43079 | 0 |  | 78 | 0.43079 | 0.044983 | 0 |  |  | 78 | 0.43079 | 0.12174 | 0 |  | 78 | 0.43079 | 0.31488 | 0 |  | 78 | 0.43079 | 0.044267 | 0
| 80 | 355.2 | 0.46737 | 0 | 0.54579 |  | 80 | 355.2 | 0.46737 | 0 |  | 80 | 355.2 | 0.46737 | 0 |  | 80 | 355.2 | 0.46737 | 0 |  | 80 | 0.46737 | 0.044983 | 0 |  |  | 80 | 0.46737 | 0.12174 | 0 |  | 80 | 0.46737 | 0.31488 | 0 |  | 80 | 0.46737 | 0.044267 | 0
| 82 | 385 | 0.50658 | 0 | 0.63859 |  | 82 | 385 | 0.50658 | 0 |  | 82 | 385 | 0.50658 | 0 |  | 82 | 385 | 0.50658 | 0 |  | 82 | 0.50658 | 0.044983 | 0 |  |  | 82 | 0.50658 | 0.12174 | 0 |  | 82 | 0.50658 | 0.31488 | 0 |  | 82 | 0.50658 | 0.044267 | 0
| 84 | 416.9 | 0.54855 | 0 | 0.75579 |  | 84 | 416.9 | 0.54855 | 0 |  | 84 | 416.9 | 0.54855 | 0 |  | 84 | 416.9 | 0.54855 | 0 |  | 84 | 0.54855 | 0.044983 | 0 |  |  | 84 | 0.54855 | 0.12174 | 0 |  | 84 | 0.54855 | 0.31488 | 0 |  | 84 | 0.54855 | 0.044267 | 0
| 86 | 450.8 | 0.59316 | 0 | 0.90685 |  | 86 | 450.8 | 0.59316 | 0 |  | 86 | 450.8 | 0.59316 | 0 |  | 86 | 450.8 | 0.59316 | 0 |  | 86 | 0.59316 | 0.044983 | 0 |  |  | 86 | 0.59316 | 0.12174 | 0 |  | 86 | 0.59316 | 0.31488 | 0 |  | 86 | 0.59316 | 0.044267 | 0
| 88 | 487.2 | 0.64105 | 0 | 1.1108 |  | 88 | 487.2 | 0.64105 | 0 |  | 88 | 487.2 | 0.64105 | 0 |  | 88 | 487.2 | 0.64105 | 0 |  | 88 | 0.64105 | 0.044983 | 0 |  |  | 88 | 0.64105 | 0.12174 | 0 |  | 88 | 0.64105 | 0.31488 | 0 |  | 88 | 0.64105 | 0.044267 | 0
| 90 | 525.9 | 0.69197 | 0 | 1.3973 |  | 90 | 525.9 | 0.69197 | 0 |  | 90 | 525.9 | 0.69197 | 0 |  | 90 | 525.9 | 0.69197 | 0 |  | 90 | 0.69197 | 0.044983 | 0 |  |  | 90 | 0.69197 | 0.12174 | 0 |  | 90 | 0.69197 | 0.31488 | 0 |  | 90 | 0.69197 | 0.044267 | 0
| 92 | 567.1 | 0.74618 | 0 | 1.8286 |  | 92 | 567.1 | 0.74618 | 0 |  | 92 | 567.1 | 0.74618 | 0 |  | 92 | 567.1 | 0.74618 | 0 |  | 92 | 0.74618 | 0.044983 | 0 |  |  | 92 | 0.74618 | 0.12174 | 0 |  | 92 | 0.74618 | 0.31488 | 0 |  | 92 | 0.74618 | 0.044267 | 0
| 94 | 611 | 0.80395 | 0 | 2.5506 |  | 94 | 611 | 0.80395 | 0 |  | 94 | 611 | 0.80395 | 0 |  | 94 | 611 | 0.80395 | 0 |  | 94 | 0.80395 | 0.044983 | 0 |  |  | 94 | 0.80395 | 0.12174 | 0 |  | 94 | 0.80395 | 0.31488 | 0 |  | 94 | 0.80395 | 0.044267 | 0
| 96 | 657.8 | 0.86553 | 0 | 4.0034 |  | 96 | 657.8 | 0.86553 | 0 |  | 96 | 657.8 | 0.86553 | 0 |  | 96 | 657.8 | 0.86553 | 0 |  | 96 | 0.86553 | 0.044983 | 0 |  |  | 96 | 0.86553 | 0.12174 | 0 |  | 96 | 0.86553 | 0.31488 | 0 |  | 96 | 0.86553 | 0.044267 | 0
| 98 | 707.3 | 0.93066 | 0 | 8.348 |  | 98 | 707.3 | 0.93066 | 0 |  | 98 | 707.3 | 0.93066 | 0 |  | 98 | 707.3 | 0.93066 | 0 |  | 98 | 0.93066 | 0.044983 | 0 |  |  | 98 | 0.93066 | 0.12174 | 0 |  | 98 | 0.93066 | 0.31488 | 0 |  | 98 | 0.93066 | 0.044267 | 0
| 100 | 760 | 1 | 0 | #DIV/0! |  | 100 | 760 | 1 | 0 |  | 100 | 760 | 1 | 0 |  | 100 | 760 | 1 | 0 |  | 100 | 1 | 0.044983 | 0 |  |  | 100 | 1 | 0.12174 | 0 |  | 100 | 1 | 0.31488 | 0 |  | 100 | 1 | 0.044267 | 0
| 110 | 1074.6 | 1.4139 | 0 |  |  | 110 | 1074.6 | 1.4139 | 0 |  | 110 | 1074.6 | 1.4139 | 0 |  | 110 | 1074.6 | 1.4139 | 0 |  | 110 | 1.4139 | 0.044983 | 0 |  |  | 110 | 1.4139 | 0.12174 | 0 |  | 110 | 1.4139 | 0.31488 | 0 |  | 110 | 1.4139 | 0.044267 | 0
| 120 | 1489.2 | 1.9595 | 0 |  |  | 120 | 1489.2 | 1.9595 | 0 |  | 120 | 1489.2 | 1.9595 | 0 |  | 120 | 1489.2 | 1.9595 | 0 |  | 120 | 1.9595 | 0.044983 | 0 |  |  | 120 | 1.9595 | 0.12174 | 0 |  | 120 | 1.9595 | 0.31488 | 0 |  | 120 | 1.9595 | 0.044267 | 0
| 130 | 2026.1 | 2.6659 | 0 |  |  | 130 | 2026.1 | 2.6659 | 0 |  | 130 | 2026.1 | 2.6659 | 0 |  | 130 | 2026.1 | 2.6659 | 0 |  | 130 | 2.6659 | 0.044983 | 0 |  |  | 130 | 2.6659 | 0.12174 | 0 |  | 130 | 2.6659 | 0.31488 | 0 |  | 130 | 2.6659 | 0.044267 | 0
| 140 | 2710.9 | 3.567 | 0 |  |  | 140 | 2710.9 | 3.567 | 0 |  | 140 | 2710.9 | 3.567 | 0 |  | 140 | 2710.9 | 3.567 | 0 |  | 140 | 3.567 | 0.044983 | 0 |  |  | 140 | 3.567 | 0.12174 | 0 |  | 140 | 3.567 | 0.31488 | 0 |  | 140 | 3.567 | 0.044267 | 0
| 150 | 3570.5 | 4.698 | 0 |  |  | 150 | 3570.5 | 4.698 | 0 |  | 150 | 3570.5 | 4.698 | 0 |  | 150 | 3570.5 | 4.698 | 0 |  | 150 | 4.698 | 0.044983 | 0 |  |  | 150 | 4.698 | 0.12174 | 0 |  | 150 | 4.698 | 0.31488 | 0 |  | 150 | 4.698 | 0.044267 | 0
| 160 | 4636 | 6.1 | 0 |  |  | 160 | 4636 | 6.1 | 0 |  | 160 | 4636 | 6.1 | 0 |  | 160 | 4636 | 6.1 | 0 |  | 160 | 6.1 | 0.044983 | 0 |  |  | 160 | 6.1 | 0.12174 | 0 |  | 160 | 6.1 | 0.31488 | 0 |  | 160 | 6.1 | 0.044267 | 0
| 170 | 5940.9 | 7.817 | 0 |  |  | 170 | 5940.9 | 7.817 | 0 |  | 170 | 5940.9 | 7.817 | 0 |  | 170 | 5940.9 | 7.817 | 0 |  | 170 | 7.817 | 0.044983 | 0 |  |  | 170 | 7.817 | 0.12174 | 0 |  | 170 | 7.817 | 0.31488 | 0 |  | 170 | 7.817 | 0.044267 | 0
| 180 | 7521 | 9.8961 | 0 |  |  | 180 | 7521 | 9.8961 | 0 |  | 180 | 7521 | 9.8961 | 0 |  | 180 | 7521 | 9.8961 | 0 |  | 180 | 9.8961 | 0.044983 | 0 |  |  | 180 | 9.8961 | 0.12174 | 0 |  | 180 | 9.8961 | 0.31488 | 0 |  | 180 | 9.8961 | 0.044267 | 0
| 190 | 9415.6 | 12.3889 | 0 |  |  | 190 | 9415.6 | 12.3889 | 0 |  | 190 | 9415.6 | 12.3889 | 0 |  | 190 | 9415.6 | 12.3889 | 0 |  | 190 | 12.3889 | 0.044983 | 0 |  |  | 190 | 12.3889 | 0.12174 | 0 |  | 190 | 12.3889 | 0.31488 | 0 |  | 190 | 12.3889 | 0.044267 | 0
| 200 | 11664.5 | 15.348 | 0 |  |  | 200 | 11664.5 | 15.348 | 0 |  | 200 | 11664.5 | 15.348 | 0 |  | 200 | 11664.5 | 15.348 | 0 |  | 200 | 15.348 | 0.044983 | 0 |  |  | 200 | 15.348 | 0.12174 | 0 |  | 200 | 15.348 | 0.31488 | 0 |  | 200 | 15.348 | 0.044267 | 0
|  |  |  | 0.072789 | [5 empty] | 0.12174 |  |  |  |  | 0.04827 |  |  |  |  | 0.072789 |  |  |  |  | 31.2538 | [5 empty] | 50 |  |  |  |  | 70.5345 |  |  |  |  | 30.9749
[25 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0 |  |  |  |  | 0
[25 empty] | 31.2538 | [5 empty] | 50 |  |  |  |  | 70.5345 |  |  |  |  | 30.9749
psdiff
7.5
| Psychrometric Table |  | Temperature
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | Temperature
| Psychrom.diff | -10 | -8 | -6 | -4 | -2 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60 | 62 | 64 | 66 | 68 | 70 | 72 | 74 | 76 | 78 | 80 | 82 | 84 | 86 | 88 | 90 | 92 | 94 | 96 | 98 | 100 | -10 | -8 | -6 | -4 | -2 | 0 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 28 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 44 | 46 | 48 | 50 | 52 | 54 | 56 | 58 | 60 | 62 | 64 | 66 | 68 | 70 | 72 | 74 | 76 | 78 | 80 | 82 | 84 | 86 | 88 | 90 | 92 | 94 | 96 | 98 | 100
1 | 0 | 95 | 96 | 97 | 97 | 98 | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0.2 | 90 | 91 | 93 | 94 | 96 | 96 | 97 | 97 | 98 | 98 | 98 | 98 | 98 | 99 | 99 | 99 | 99 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | 99.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0.4 | 84 | 85 | 87 | 90 | 92 | 92 | 94 | 94 | 95 | 95 | 95 | 96 | 96 | 97 | 97 | 97 | 97 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | 98.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0.5 | 81.5 | 82.5 | 84.5 | 87.5 | 90 | 90.5 | 92.5 | 93 | 93.5 | 93.5 | 93.5 | 94.5 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.6 | 79 | 80 | 82 | 85 | 88 | 89 | 91 | 92 | 92 | 92 | 92 | 93 | 94 | 95 | 95 | 95 | 95 | 94.6667 | 94.6667 | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 96 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 96.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | 97.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0.8 | 73 | 75 | 77 | 81 | 84 | 85 | 86 | 89 | 89 | 89 | 90 | 91 | 92 | 93 | 93 | 93 | 93 | 93.3333 | 93.3333 | 94 | 94 | 94 | 94 | 94 | 95 | 95 | 95 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 95.6667 | 96.6667 | 96.6667 | 96.6667 | 96.6667 | 96.6667 | 96.6667 | 96.6667 | 96.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 1 | 67 | 70 | 73 | 77 | 80 | 82 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 91 | 91 | 91 | 92 | 92 | 93 | 93 | 93 | 93 | 93 | 94 | 94 | 94 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 1.2 | 61 | 64 | 68 | 73 | 76 | 78 | 80 | 83 | 83 | 84 | 85 | 87 | 88 | 89 | 89 | 90 | 90 | 90.6667 | 90.6667 | 91.3333 | 91.6667 | 91.6667 | 91.6667 | 92 | 93 | 93.3333 | 93.3333 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94.3333 | 94.3333 | 94.3333 | 94.3333 | 94.3333 | 94.3333 | 95.3333 | 95.3333 | 95.3333 | 95.3333 | 95.3333 | 95.3333 | 95.3333 | 95.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 1.4 | 54 | 59 | 64 | 69 | 72 | 74 | 77 | 80 | 80 | 81 | 83 | 85 | 86 | 87 | 87 | 88 | 88 | 89.3333 | 89.3333 | 89.6667 | 90.3333 | 90.3333 | 90.3333 | 91 | 92 | 92.6667 | 92.6667 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93.6667 | 93.6667 | 93.6667 | 93.6667 | 93.6667 | 93.6667 | 94.6667 | 94.6667 | 94.6667 | 94.6667 | 94.6667 | 94.6667 | 94.6667 | 94.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 1.5 | 51 | 56.5 | 61.5 | 67 | 70.5 | 72.5 | 76 | 78.5 | 79 | 80 | 81.5 | 83.5 | 85 | 86 | 86 | 87 | 87 | 88 | 88 | 88 | 89 | 89 | 89 | 90 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 93 | 93 | 93 | 93 | 93 | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 1.6 | 48 | 54 | 59 | 65 | 69 | 71 | 75 | 77 | 78 | 79 | 80 | 82 | 84 | 85 | 85 | 86 | 86 | 86.6667 | 86.6667 | 87 | 88 | 88 | 88.3333 | 89 | 90 | 90.6667 | 91 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 92.3333 | 92.3333 | 92.3333 | 92.3333 | 92.3333 | 92.3333 | 93.3333 | 93.3333 | 93.3333 | 93.3333 | 93.3333 | 93.3333 | 93.3333 | 93.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 1.8 | 43 | 49 | 55 | 61 | 65 | 68 | 72 | 74 | 75 | 77 | 78 | 80 | 82 | 83 | 83 | 84 | 85 | 85.3333 | 85.3333 | 86 | 87 | 87 | 87.6667 | 88 | 89 | 89.3333 | 90 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 91.6667 | 91.6667 | 91.6667 | 91.6667 | 91.6667 | 91.6667 | 92.6667 | 92.6667 | 92.6667 | 92.6667 | 92.6667 | 92.6667 | 92.6667 | 92.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 2 | 38 | 45 | 51 | 57 | 62 | 65 | 68 | 71 | 73 | 75 | 76 | 78 | 80 | 81 | 81 | 82 | 83 | 84 | 84 | 85 | 86 | 86 | 87 | 87 | 88 | 88 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 2.2 | 32 | 41 | 47 | 53 | 58 | 61 | 64 | 68 | 70 | 72 | 74 | 76 | 78 | 79 | 80 | 81 | 81 | 82.6667 | 83 | 84 | 85 | 85 | 86 | 86.3333 | 87 | 87 | 88 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89.3333 | 90 | 90 | 90 | 90 | 90 | 90 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | 91.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 2.4 | 26 | 37 | 43 | 49 | 55 | 57 | 61 | 65 | 67 | 70 | 72 | 74 | 76 | 77 | 78 | 80 | 80 | 81.3333 | 82 | 83 | 84 | 84 | 85 | 85.6667 | 86 | 86 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88.6667 | 89 | 89 | 89 | 89 | 89 | 89 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | 90.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 2.5 | 23 | 34.5 | 41 | 47 | 53 | 55.5 | 60 | 64 | 66 | 69 | 71 | 73 | 75 | 76.5 | 77.5 | 79 | 79.5 | 80 | 81 | 82 | 83 | 83 | 84 | 85 | 85 | 85 | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 2.6 | 20 | 32 | 39 | 45 | 51 | 54 | 59 | 63 | 65 | 68 | 70 | 72 | 74 | 76 | 77 | 78 | 79 | 78.6667 | 79.6667 | 80.6667 | 81.6667 | 82 | 83 | 83.6667 | 84 | 84 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86.3333 | 86.3333 | 86.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 89.3333 | 89.3333 | 89.3333 | 89.3333 | 89.3333 | 89.3333 | 89.3333 | 89.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 2.8 | 15 | 27 | 35 | 41 | 47 | 51 | 56 | 60 | 62 | 65 | 67 | 70 | 72 | 74 | 75 | 76 | 77 | 77.3333 | 78.3333 | 79.3333 | 80.3333 | 81 | 82 | 82.3333 | 83 | 83 | 84 | 85 | 85 | 85 | 85 | 85 | 85 | 85.6667 | 85.6667 | 85.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 88.6667 | 88.6667 | 88.6667 | 88.6667 | 88.6667 | 88.6667 | 88.6667 | 88.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 3 | 10 | 22 | 32 | 38 | 44 | 48 | 53 | 58 | 60 | 63 | 65 | 68 | 70 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 81 | 82 | 82 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 85 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 3.2 | 0 | 18 | 28 | 34 | 41 | 45 | 49 | 54 | 57 | 60 | 63 | 66 | 68 | 70 | 72 | 72 | 74 | 74.6667 | 75.6667 | 76.6667 | 77.6667 | 78.6667 | 80 | 80.3333 | 81 | 81 | 82 | 83 | 83 | 83 | 83 | 83.3333 | 83.3333 | 84.3333 | 84.3333 | 84.3333 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.6667 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | 87.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 3.4 | 0 | 14 | 24 | 30 | 37 | 42 | 47 | 52 | 54 | 58 | 61 | 64 | 66 | 68 | 70 | 70 | 72 | 73.3333 | 74.3333 | 75.3333 | 76.3333 | 77.3333 | 79 | 79.6667 | 80 | 80 | 81 | 82 | 82 | 82 | 82 | 82.6667 | 82.6667 | 83.6667 | 83.6667 | 83.6667 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 85.3333 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | 86.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 3.5 | 0 | 0 | 22.5 | 28.5 | 35.5 | 40.5 | 45.5 | 50 | 53 | 56.5 | 60 | 63 | 65 | 67 | 69 | 69.5 | 71.5 | 72 | 73 | 74 | 75 | 76 | 78 | 79 | 79 | 79 | 80 | 81 | 81 | 81 | 81 | 82 | 82 | 83 | 83 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 3.6 | 0 | 0 | 21 | 27 | 34 | 39 | 44 | 48 | 52 | 55 | 59 | 62 | 64 | 66 | 68 | 69 | 71 | 71 | 72 | 73 | 74 | 75.3333 | 77 | 77.6667 | 78 | 78.3333 | 79.3333 | 80.3333 | 80.3333 | 80.3333 | 80.3333 | 81.3333 | 81.3333 | 82.3333 | 82.3333 | 82.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 83.6667 | 84.6667 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.3333 | 85.6667 | 85.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 3.8 | 0 | 0 | 18 | 24 | 31 | 36 | 41 | 46 | 50 | 53 | 57 | 60 | 62 | 64 | 66 | 68 | 69 | 70 | 71 | 72 | 73 | 74.6667 | 76 | 76.3333 | 77 | 77.6667 | 78.6667 | 79.6667 | 79.6667 | 79.6667 | 79.6667 | 80.6667 | 80.6667 | 81.6667 | 81.6667 | 81.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 83.3333 | 84.3333 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 84.6667 | 85.3333 | 85.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 4 | 0 | 0 | 15 | 22 | 29 | 33 | 39 | 43 | 47 | 51 | 54 | 57 | 60 | 62 | 64 | 66 | 68 | 69 | 70 | 71 | 72 | 74 | 75 | 75 | 76 | 77 | 78 | 79 | 79 | 79 | 79 | 80 | 80 | 81 | 81 | 81 | 82 | 82 | 82 | 82 | 82 | 83 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 85 | 85 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 4.2 | 0 | 0 | 0 | 19 | 26 | 30 | 36 | 41 | 45 | 48 | 52 | 55 | 58 | 60 | 62 | 64 | 66 | 67.6667 | 68.6667 | 69.6667 | 71 | 73 | 74 | 74 | 75 | 76 | 77 | 78 | 78 | 78 | 78 | 79 | 79.3333 | 80.3333 | 80.3333 | 80.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 82.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 83.3333 | 84.3333 | 84.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 4.4 | 0 | 0 | 0 | 16 | 24 | 27 | 33 | 39 | 42 | 46 | 50 | 53 | 56 | 58 | 60 | 63 | 65 | 66.3333 | 67.3333 | 68.3333 | 70 | 72 | 73 | 73 | 74 | 75 | 76 | 77 | 77 | 77 | 77 | 78 | 78.6667 | 79.6667 | 79.6667 | 79.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 81.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 82.6667 | 83.6667 | 83.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 4.5 | 0 | 0 | 0 | 14.5 | 22.5 | 26 | 32 | 37.5 | 41 | 45 | 49 | 52 | 55 | 57.5 | 59.5 | 62 | 64 | 65 | 66 | 67 | 69 | 71 | 72 | 72 | 73 | 74 | 75 | 76 | 76 | 76 | 76 | 77 | 78 | 79 | 79 | 79 | 80 | 80 | 80 | 80 | 80 | 81 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 83 | 83 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 4.6 | 0 | 0 | 0 | 13 | 21 | 25 | 31 | 36 | 40 | 44 | 48 | 51 | 54 | 57 | 59 | 61 | 63 | 64 | 65.3333 | 66.3333 | 68 | 70 | 71 | 71 | 72 | 73 | 74 | 75 | 75.3333 | 75.3333 | 75.3333 | 76.3333 | 77.3333 | 78.3333 | 78.3333 | 78.3333 | 79.3333 | 79.3333 | 79.3333 | 79.3333 | 79.3333 | 80.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 81.3333 | 82.3333 | 82.3333 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 4.8 | 0 | 0 | 0 | 11 | 19 | 22 | 28 | 33 | 38 | 42 | 46 | 50 | 53 | 55 | 58 | 60 | 62 | 63 | 64.6667 | 65.6667 | 67 | 69 | 70 | 70 | 71 | 72 | 73 | 74 | 74.6667 | 74.6667 | 74.6667 | 75.6667 | 76.6667 | 77.6667 | 77.6667 | 77.6667 | 78.6667 | 78.6667 | 78.6667 | 78.6667 | 78.6667 | 79.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 80.6667 | 81.6667 | 81.6667 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 5 | 0 | 0 | 0 | 9 | 17 | 20 | 25 | 31 | 36 | 40 | 44 | 48 | 51 | 54 | 56 | 58 | 60 | 62 | 64 | 65 | 66 | 68 | 69 | 69 | 70 | 71 | 72 | 73 | 74 | 74 | 74 | 75 | 76 | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 79 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 5.5 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 25 | 30 | 35 | 39 | 43 | 47 | 49 | 51 | 54 | 57 | 59 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 70 | 71 | 72 | 72 | 72 | 73 | 74 | 75 | 75 | 75 | 76 | 76 | 76 | 76 | 76 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 79 | 79 | 80 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 18 | 25 | 30 | 34 | 38 | 42 | 46 | 48 | 51 | 54 | 56 | 58 | 59 | 61 | 62 | 63 | 64 | 65 | 66 | 68 | 68 | 70 | 70 | 70 | 71 | 72 | 73 | 73 | 73 | 74 | 74 | 75 | 75 | 75 | 76 | 76 | 77 | 77 | 77 | 77 | 77 | 78 | 78 | 79 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | 6.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 19 | 25 | 29 | 33 | 38 | 42 | 45 | 47 | 50 | 52 | 54 | 56 | 58 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 68 | 69 | 70 | 70 | 71 | 71 | 72 | 72 | 73 | 73 | 73 | 74 | 74 | 75 | 75 | 75 | 75 | 75 | 76 | 76 | 77 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 14 | 20 | 24 | 29 | 34 | 38 | 41 | 44 | 46 | 49 | 51 | 53 | 55 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 68 | 69 | 69 | 70 | 70 | 71 | 71 | 71 | 72 | 72 | 73 | 73 | 73 | 74 | 74 | 74 | 75 | 75 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 19 | 24 | 30 | 34 | 37 | 40 | 43 | 46 | 48 | 51 | 53 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 62 | 64 | 65 | 66 | 66 | 67 | 67 | 68 | 68 | 69 | 69 | 69 | 70 | 70 | 71 | 71 | 71 | 72 | 72 | 73 | 73 | 73 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 19 | 24 | 30 | 34 | 37 | 40 | 43 | 46 | 48 | 51 | 53 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 62 | 64 | 65 | 66 | 66 | 67 | 67 | 68 | 68 | 69 | 69 | 69 | 70 | 70 | 71 | 71 | 71 | 72 | 72 | 73 | 73 | 73 | 0 | 0 | 0 | 0 | 0
37 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 10 | 15 | 20 | 25 | 30 | 34 | 36 | 40 | 43 | 45 | 47 | 50 | 52 | 53 | 54 | 55 | 56 | 58 | 59 | 60 | 60 | 62 | 63 | 64 | 64 | 65 | 65 | 66 | 67 | 67 | 68 | 68 | 69 | 69 | 70 | 70 | 70 | 71 | 71 | 72 | 72 | 72 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 22 | 26 | 31 | 33 | 37 | 40 | 43 | 45 | 47 | 49 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 60 | 61 | 62 | 62 | 63 | 63 | 64 | 65 | 65 | 66 | 66 | 67 | 67 | 68 | 68 | 68 | 69 | 69 | 70 | 70 | 70 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 18 | 23 | 27 | 30 | 34 | 37 | 40 | 42 | 44 | 46 | 48 | 49 | 50 | 51 | 53 | 54 | 55 | 56 | 58 | 59 | 60 | 60 | 61 | 61 | 62 | 63 | 63 | 64 | 64 | 65 | 65 | 66 | 66 | 66 | 67 | 67 | 68 | 69 | 69 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 19 | 24 | 27 | 31 | 34 | 37 | 40 | 42 | 44 | 46 | 48 | 49 | 49 | 51 | 52 | 53 | 54 | 56 | 57 | 58 | 58 | 59 | 59 | 60 | 61 | 62 | 62 | 62 | 63 | 64 | 65 | 65 | 65 | 66 | 66 | 67 | 67 | 67 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
41 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16 | 20 | 24 | 28 | 31 | 34 | 37 | 40 | 42 | 44 | 45 | 46 | 47 | 49 | 50 | 51 | 52 | 54 | 55 | 56 | 57 | 58 | 58 | 59 | 60 | 61 | 61 | 61 | 63 | 63 | 64 | 64 | 64 | 65 | 65 | 66 | 66 | 66 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
42 | 10.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 20 | 25 | 28.5 | 31.5 | 34.5 | 37.5 | 39.5 | 41.5 | 42.5 | 44 | 45 | 47 | 48 | 49 | 50 | 52 | 53 | 54 | 55 | 56 | 56.5 | 57.5 | 58.5 | 59 | 59.5 | 59.5 | 61 | 61.5 | 62.5 | 62.5 | 62.5 | 63.5 | 63.5 | 64.5 | 64.5 | 64.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 13 | 17 | 22 | 26 | 29 | 32 | 35 | 37 | 39 | 40 | 42 | 43 | 45 | 46 | 47 | 48 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 57 | 58 | 58 | 59 | 60 | 61 | 61 | 61 | 62 | 62 | 63 | 63 | 63 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15 | 19 | 23 | 26.5 | 29.5 | 32.5 | 34.5 | 36.5 | 38 | 40 | 41.5 | 43.5 | 44.5 | 46 | 47 | 48.5 | 49.5 | 50.5 | 51.5 | 52.5 | 53.5 | 54.5 | 55.5 | 55.5 | 56.5 | 56.5 | 57.5 | 58.5 | 59.5 | 59.5 | 59.5 | 60.5 | 60.5 | 61.5 | 61.5 | 62 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 11 | 16 | 20 | 24 | 27 | 30 | 32 | 34 | 36 | 38 | 40 | 42 | 43 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 54 | 55 | 55 | 56 | 57 | 58 | 58 | 58 | 59 | 59 | 60 | 60 | 61 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 17.5 | 21.5 | 24.5 | 27.5 | 29.5 | 31.5 | 34 | 36 | 38 | 40 | 41 | 43 | 44 | 45.5 | 46.5 | 47.5 | 48.5 | 49.5 | 50.5 | 51.5 | 52.5 | 53 | 53.5 | 53.5 | 54.5 | 55 | 56 | 56.5 | 56.5 | 57.5 | 57.5 | 58.5 | 58.5 | 59.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
47 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 19 | 22 | 25 | 27 | 29 | 32 | 34 | 36 | 38 | 39 | 41 | 42 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 52 | 53 | 53 | 54 | 55 | 55 | 56 | 56 | 57 | 57 | 58 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14 | 17 | 20 | 23 | 26 | 28 | 30 | 32 | 35 | 36 | 38 | 39 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 49 | 49 | 50 | 51 | 52 | 53 | 53 | 54 | 54 | 55 | 55 | 56 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
49 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 16 | 19 | 22 | 24 | 26 | 28 | 31 | 33 | 34 | 36 | 37 | 38 | 39 | 41 | 42 | 43 | 44 | 45 | 46 | 46 | 46 | 47 | 48 | 49 | 50 | 50 | 51 | 51 | 52 | 52 | 53 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 16 | 18 | 21 | 23 | 25 | 28 | 30 | 31 | 33 | 34 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 44 | 45 | 46 | 47 | 48 | 48 | 49 | 49 | 50 | 50 | 51 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 15 | 17 | 20 | 22 | 25 | 27 | 28 | 30 | 31 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 41 | 42 | 43 | 44 | 45 | 45 | 46 | 46 | 47 | 48 | 49 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 17 | 19 | 22 | 24 | 25 | 27 | 29 | 30 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 39 | 40 | 41 | 42 | 43 | 43 | 44 | 44 | 45 | 46 | 47 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 21 | 22 | 24 | 26 | 27 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 40 | 41 | 42 | 42 | 43 | 44 | 45 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 16 | 18 | 20 | 22 | 24 | 25 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 38 | 39 | 40 | 40 | 41 | 42 | 43 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 13 | 15 | 17 | 19 | 21 | 22 | 24 | 25 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 36 | 37 | 38 | 38 | 39 | 40 | 41 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 13 | 15 | 17 | 19 | 20 | 22 | 23 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 34 | 35 | 36 | 36 | 37 | 38 | 39 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 14 | 16 | 18 | 20 | 21 | 22.5 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 32.5 | 33 | 34 | 34 | 35 | 36 | 37 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 12 | 14 | 16 | 18 | 19 | 20 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 31 | 32 | 32 | 33 | 34 | 35 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 14 | 16 | 17 | 18.5 | 20 | 21 | 22 | 23.5 | 24.5 | 25 | 26.5 | 27 | 28 | 29 | 29.5 | 30.5 | 30.5 | 31.5 | 32.5 | 33.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 12 | 14 | 15 | 17 | 18 | 19 | 20 | 22 | 23 | 23 | 25 | 25 | 26 | 27 | 28 | 29 | 29 | 30 | 31 | 32 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 13 | 15 | 16 | 17.5 | 18.5 | 20 | 21 | 21.5 | 23 | 23.5 | 24.5 | 25.5 | 26.5 | 27.5 | 27.5 | 28.5 | 29.5 | 30.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 12 | 13 | 14 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 27 | 28 | 29 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 11 | 12.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5 | 20.5 | 21.5 | 22.5 | 23.5 | 24.5 | 24.5 | 25.5 | 26.5 | 27.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 8 | 9 | 11 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 23 | 24 | 25 | 26 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 11.5 | 12.5 | 13.5 | 14.5 | 15.5 | 16.5 | 17.5 | 18.5 | 19.5 | 20.5 | 21.5 | 21.5 | 22.5 | 23.5 | 24.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 20 | 21 | 22 | 23 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 12 | 13 | 14 | 15 | 16 | 16.5 | 17.5 | 18.5 | 19 | 20 | 20.5 | 21.5 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 16 | 17 | 18 | 19 | 19 | 20 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.5 | 11.5 | 12.5 | 13.5 | 14 | 15 | 16 | 16.5 | 17.5 | 18 | 19 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 16 | 17 | 18 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 13 | 14 | 14 | 15 | 16 | 17 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 12 | 13 | 13 | 14 | 15 | 16 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 13 | 14 | 15 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 11 | 12 | 13 | 14 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 15 | 19 | 24 | 30 | 34 | 37 | 40 | 43 | 46 | 48 | 51 | 53 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 62 | 64 | 65 | 66 | 66 | 67 | 67 | 68 | 68 | 69 | 69 | 69 | 70 | 70 | 71 | 71 | 71 | 72 | 72 | 73 | 73 | 73 | 0 | 0 | 0 | 0 | 0 | bar: Temperature 10 8; Temperature 15 18; Temperature 20 28; Temperature 26 40; Temperature 31 50
RH | bar: Temperature 10 8; Temperature 15 18; Temperature 20 28; Temperature 26 40; Temperature 31 50
[58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | bar: Temperature 10 8; Temperature 15 18; Temperature 20 28; Temperature 26 40; Temperature 31 50