## Calculation
Starting conditions (Condition no 1) :
pressure (absolute) | 1 | bar (absolute) | OK
Temperature (degr Celcius) | 35 | degr.Celcius
Relative humidity % | 100 | %
Saturated water vapor pressure | 0.055487 | bar
Vapor pressure | 0.055487 | bar
pressure dry air | 0.94451 | bar
density dry air | 1.0825 | kg/m3
specific volume dry air | 0.92381 | m3/kg
Water vapor content | 0.03654 | kg/kg(dry air)
Total mass dry air + vapor | 1.0365 | kg
density starting conditions | 1.122 | kg/m3
specific volume at intake conditions | 0.89124 | m3/kg
Local conditions (Condition no 2) :
pressure (absolute) | 2 | bar (absolute) | OK
Temperature (degr Celcius) | 20 | degr. Celcius
Relative humidity % | 100 | %
Saturated water vapor pressure | 0.023066 | bar
Vapor pressure | 0.023066 | bar
pressure dry air | 1.9769 | bar
density dry air | 2.3817 | kg/m3
specific volume dry air | 0.41987 | m3/kg
Water vapor content | 0.0072572 | kg/kg(dry air)
Total mass dry air + vapor | 1.0073 | kg
density local conditions | 2.399 | kg/m3
Condensated mass of water | 0.029283 | kg/kg(dry air)
Volume of transport intake air | 2500 | m3/hr
Conveyed material | 1500 | tons/hr
Condensated water | 79.2458 | kg/hr
Bonded mass of cement | 334.4175 | kg/hr
| 0.022294 | %
RH-calculation from wet bulb temperature
pressure (absolute) | 1 | bar (absolute)
Ambient temperature (degr Celcius) | 40 | degr. Celcius | OK
Wet bulb temperature | 28.2157 | degr. Celcius | OK
Psychometric difference | 11.7843 | degr. Celcius
Saturated water vapor pressure tamb | 0.072789 | bar
Water vapor content | 0.024415 | kg/kg(dry air)
Saturated water vapor pressure temp wet | 0.037769 | bar
Water vapor content | 0.024415 | kg/kg(dry air)
pressure dry air ambient | 0.96361 | bar
density dry air | 1.0867 | kg/m3
specific volume dry air | 0.9202 | m3/kg
Total mass dry air + vapor | 1.0244 | kg
density local conditions | 0.89827 | kg/m3
Relative humidity % | 49.9997 | %
Note on C38: Remark: Volume of pneumatic conveying compressor or Volume in silo above cement
Note on C39: Remark: Capacity rate or mass of product

## Table
|  |  | Pressure | 1 | [7 empty] | Pressure |  |  |  | Pressure
| saturated | saturated | relative humidity | 100% |  | saturated | saturated |  |  | saturated | saturated | relative humidity |  | saturated | saturated | relative humidity |  | saturated
temperature | water vapour pressure | water vapour pressure |  | Saturared water | temperature | water vapour pressure | water vapour pressure |  | temperature | water vapour pressure | water vapour pressure |  | temperature | water vapour pressure | water vapour pressure |  | temperature | water vapour pressure
| inch Hg | bar |  | content |  | inch Hg | bar |  |  | inch Hg | bar |  |  | inch Hg | bar |  |  | bar
-55 | 0.015 | 1.9737e-05 | 0 | 1.2277e-05 | -55 | 0.015 | 1.9737e-05 | 0 | -55 | 0.015 | 1.9737e-05 | 0 | -55 | 0.015 | 1.9737e-05 | 0 | -55 | 1.9737e-05
-50 | 0.029 | 3.8158e-05 | 0 | 2.3735e-05 | -50 | 0.029 | 3.8158e-05 | 0 | -50 | 0.029 | 3.8158e-05 | 0 | -50 | 0.029 | 3.8158e-05 | 0 | -50 | 3.8158e-05
-45 | 0.052 | 6.8421e-05 | 0 | 4.2561e-05 | -45 | 0.052 | 6.8421e-05 | 0 | -45 | 0.052 | 6.8421e-05 | 0 | -45 | 0.052 | 6.8421e-05 | 0 | -45 | 6.8421e-05
-40 | 0.093 | 0.00012237 | 0 | 7.6122e-05 | -40 | 0.093 | 0.00012237 | 0 | -40 | 0.093 | 0.00012237 | 0 | -40 | 0.093 | 0.00012237 | 0 | -40 | 0.00012237
-38 | 0.119 | 0.00015658 | 0 | 9.7407e-05 | -38 | 0.119 | 0.00015658 | 0 | -38 | 0.119 | 0.00015658 | 0 | -38 | 0.119 | 0.00015658 | 0 | -38 | 0.00015658
-36 | 0.15 | 0.00019737 | 0 | 0.00012279 | -36 | 0.15 | 0.00019737 | 0 | -36 | 0.15 | 0.00019737 | 0 | -36 | 0.15 | 0.00019737 | 0 | -36 | 0.00019737
-34 | 0.185 | 0.00024342 | 0 | 0.00015144 | -34 | 0.185 | 0.00024342 | 0 | -34 | 0.185 | 0.00024342 | 0 | -34 | 0.185 | 0.00024342 | 0 | -34 | 0.00024342
-32 | 0.227 | 0.00029868 | 0 | 0.00018584 | -32 | 0.227 | 0.00029868 | 0 | -32 | 0.227 | 0.00029868 | 0 | -32 | 0.227 | 0.00029868 | 0 | -32 | 0.00029868
-30 | 0.28 | 0.00036842 | 0 | 0.00022924 | -30 | 0.28 | 0.00036842 | 0 | -30 | 0.28 | 0.00036842 | 0 | -30 | 0.28 | 0.00036842 | 0 | -30 | 0.00036842
-28 | 0.345 | 0.00045395 | 0 | 0.00028248 | -28 | 0.345 | 0.00045395 | 0 | -28 | 0.345 | 0.00045395 | 0 | -28 | 0.345 | 0.00045395 | 0 | -28 | 0.00045395
-26 | 0.425 | 0.00055921 | 0 | 0.00034802 | -26 | 0.425 | 0.00055921 | 0 | -26 | 0.425 | 0.00055921 | 0 | -26 | 0.425 | 0.00055921 | 0 | -26 | 0.00055921
-24 | 0.521 | 0.00068553 | 0 | 0.00042669 | -24 | 0.521 | 0.00068553 | 0 | -24 | 0.521 | 0.00068553 | 0 | -24 | 0.521 | 0.00068553 | 0 | -24 | 0.00068553
-22 | 0.636 | 0.00083684 | 0 | 0.00052095 | -22 | 0.636 | 0.00083684 | 0 | -22 | 0.636 | 0.00083684 | 0 | -22 | 0.636 | 0.00083684 | 0 | -22 | 0.00083684
-20 | 0.772 | 0.0010158 | 0 | 0.00063246 | -20 | 0.772 | 0.0010158 | 0 | -20 | 0.772 | 0.0010158 | 0 | -20 | 0.772 | 0.0010158 | 0 | -20 | 0.0010158
-19 | 0.85 | 0.0011184 | 0 | 0.00069644 | -19 | 0.85 | 0.0011184 | 0 | -19 | 0.85 | 0.0011184 | 0 | -19 | 0.85 | 0.0011184 | 0 | -19 | 0.0011184
-18 | 0.935 | 0.0012303 | 0 | 0.00076617 | -18 | 0.935 | 0.0012303 | 0 | -18 | 0.935 | 0.0012303 | 0 | -18 | 0.935 | 0.0012303 | 0 | -18 | 0.0012303
-17 | 1.027 | 0.0013513 | 0 | 0.00084166 | -17 | 1.027 | 0.0013513 | 0 | -17 | 1.027 | 0.0013513 | 0 | -17 | 1.027 | 0.0013513 | 0 | -17 | 0.0013513
-16 | 1.128 | 0.0014842 | 0 | 0.00092455 | -16 | 1.128 | 0.0014842 | 0 | -16 | 1.128 | 0.0014842 | 0 | -16 | 1.128 | 0.0014842 | 0 | -16 | 0.0014842
-15 | 1.238 | 0.0016289 | 0 | 0.0010149 | -15 | 1.238 | 0.0016289 | 0 | -15 | 1.238 | 0.0016289 | 0 | -15 | 1.238 | 0.0016289 | 0 | -15 | 0.0016289
-14 | 1.357 | 0.0017855 | 0 | 0.0011126 | -14 | 1.357 | 0.0017855 | 0 | -14 | 1.357 | 0.0017855 | 0 | -14 | 1.357 | 0.0017855 | 0 | -14 | 0.0017855
-13 | 1.486 | 0.0019553 | 0 | 0.0012186 | -13 | 1.486 | 0.0019553 | 0 | -13 | 1.486 | 0.0019553 | 0 | -13 | 1.486 | 0.0019553 | 0 | -13 | 0.0019553
-12 | 1.627 | 0.0021408 | 0 | 0.0013344 | -12 | 1.627 | 0.0021408 | 0 | -12 | 1.627 | 0.0021408 | 0 | -12 | 1.627 | 0.0021408 | 0 | -12 | 0.0021408
-11 | 1.78 | 0.0023421 | 0 | 0.0014602 | -11 | 1.78 | 0.0023421 | 0 | -11 | 1.78 | 0.0023421 | 0 | -11 | 1.78 | 0.0023421 | 0 | -11 | 0.0023421
-10 | 1.946 | 0.0025605 | 0 | 0.0015967 | -10 | 1.946 | 0.0025605 | 0 | -10 | 1.946 | 0.0025605 | 0 | -10 | 1.946 | 0.0025605 | 0 | -10 | 0.0025605
-9 | 2.125 | 0.0027961 | 0 | 0.001744 | -9 | 2.125 | 0.0027961 | 0 | -9 | 2.125 | 0.0027961 | 0 | -9 | 2.125 | 0.0027961 | 0 | -9 | 0.0027961
-8 | 2.321 | 0.0030539 | 0 | 0.0019054 | -8 | 2.321 | 0.0030539 | 0 | -8 | 2.321 | 0.0030539 | 0 | -8 | 2.321 | 0.0030539 | 0 | -8 | 0.0030539
-7 | 2.532 | 0.0033316 | 0 | 0.0020792 | -7 | 2.532 | 0.0033316 | 0 | -7 | 2.532 | 0.0033316 | 0 | -7 | 2.532 | 0.0033316 | 0 | -7 | 0.0033316
-6 | 2.761 | 0.0036329 | 0 | 0.0022679 | -6 | 2.761 | 0.0036329 | 0 | -6 | 2.761 | 0.0036329 | 0 | -6 | 2.761 | 0.0036329 | 0 | -6 | 0.0036329
-5 | 3.008 | 0.0039579 | 0 | 0.0024716 | -5 | 3.008 | 0.0039579 | 0 | -5 | 3.008 | 0.0039579 | 0 | -5 | 3.008 | 0.0039579 | 0 | -5 | 0.0039579
-4 | 3.275 | 0.0043092 | 0 | 0.0026919 | -4 | 3.275 | 0.0043092 | 0 | -4 | 3.275 | 0.0043092 | 0 | -4 | 3.275 | 0.0043092 | 0 | -4 | 0.0043092
-3 | 3.566 | 0.0046921 | 0 | 0.0029322 | -3 | 3.566 | 0.0046921 | 0 | -3 | 3.566 | 0.0046921 | 0 | -3 | 3.566 | 0.0046921 | 0 | -3 | 0.0046921
-2 | 3.879 | 0.0051039 | 0 | 0.0031909 | -2 | 3.879 | 0.0051039 | 0 | -2 | 3.879 | 0.0051039 | 0 | -2 | 3.879 | 0.0051039 | 0 | -2 | 0.0051039
-1 | 4.216 | 0.0055474 | 0 | 0.0034697 | -1 | 4.216 | 0.0055474 | 0 | -1 | 4.216 | 0.0055474 | 0 | -1 | 4.216 | 0.0055474 | 0 | -1 | 0.0055474
0 | 4.581 | 0.0060276 | 0 | 0.0037719 | 0 | 4.581 | 0.0060276 | 0 | 0 | 4.581 | 0.0060276 | 0 | 0 | 4.581 | 0.0060276 | 0 | 0 | 0.0060276
1 | 4.924 | 0.0064789 | 0 | 0.0040562 | 1 | 4.924 | 0.0064789 | 0 | 1 | 4.924 | 0.0064789 | 0 | 1 | 4.924 | 0.0064789 | 0 | 1 | 0.0064789
2 | 5.291 | 0.0069618 | 0 | 0.0043606 | 2 | 5.291 | 0.0069618 | 0 | 2 | 5.291 | 0.0069618 | 0 | 2 | 5.291 | 0.0069618 | 0 | 2 | 0.0069618
3 | 5.681 | 0.007475 | 0 | 0.0046845 | 3 | 5.681 | 0.007475 | 0 | 3 | 5.681 | 0.007475 | 0 | 3 | 5.681 | 0.007475 | 0 | 3 | 0.007475
4 | 6.097 | 0.0080224 | 0 | 0.0050303 | 4 | 6.097 | 0.0080224 | 0 | 4 | 6.097 | 0.0080224 | 0 | 4 | 6.097 | 0.0080224 | 0 | 4 | 0.0080224
5 | 6.539 | 0.0086039 | 0 | 0.0053981 | 5 | 6.539 | 0.0086039 | 0 | 5 | 6.539 | 0.0086039 | 0 | 5 | 6.539 | 0.0086039 | 0 | 5 | 0.0086039
7 | 7.51 | 0.0098816 | 0 | 0.0062077 | 7 | 7.51 | 0.0098816 | 0 | 7 | 7.51 | 0.0098816 | 0 | 7 | 7.51 | 0.0098816 | 0 | 7 | 0.0098816
8 | 8.041 | 0.01058 | 0 | 0.0066513 | 8 | 8.041 | 0.01058 | 0 | 8 | 8.041 | 0.01058 | 0 | 8 | 8.041 | 0.01058 | 0 | 8 | 0.01058
9 | 8.606 | 0.011324 | 0 | 0.007124 | 9 | 8.606 | 0.011324 | 0 | 9 | 8.606 | 0.011324 | 0 | 9 | 8.606 | 0.011324 | 0 | 9 | 0.011324
10 | 9.204 | 0.012111 | 0 | 0.0076251 | 10 | 9.204 | 0.012111 | 0 | 10 | 9.204 | 0.012111 | 0 | 10 | 9.204 | 0.012111 | 0 | 10 | 0.012111
11 | 9.839 | 0.012946 | 0 | 0.0081581 | 11 | 9.839 | 0.012946 | 0 | 11 | 9.839 | 0.012946 | 0 | 11 | 9.839 | 0.012946 | 0 | 11 | 0.012946
12 | 10.512 | 0.013832 | 0 | 0.0087239 | 12 | 10.512 | 0.013832 | 0 | 12 | 10.512 | 0.013832 | 0 | 12 | 10.512 | 0.013832 | 0 | 12 | 0.013832
13 | 11.226 | 0.014771 | 0 | 0.0093253 | 13 | 11.226 | 0.014771 | 0 | 13 | 11.226 | 0.014771 | 0 | 13 | 11.226 | 0.014771 | 0 | 13 | 0.014771
14 | 11.982 | 0.015766 | 0 | 0.0099634 | 14 | 11.982 | 0.015766 | 0 | 14 | 11.982 | 0.015766 | 0 | 14 | 11.982 | 0.015766 | 0 | 14 | 0.015766
15 | 12.781 | 0.016817 | 0 | 0.010639 | 15 | 12.781 | 0.016817 | 0 | 15 | 12.781 | 0.016817 | 0 | 15 | 12.781 | 0.016817 | 0 | 15 | 0.016817
16 | 13.628 | 0.017932 | 0 | 0.011357 | 16 | 13.628 | 0.017932 | 0 | 16 | 13.628 | 0.017932 | 0 | 16 | 13.628 | 0.017932 | 0 | 16 | 0.017932
17 | 14.524 | 0.019111 | 0 | 0.012118 | 17 | 14.524 | 0.019111 | 0 | 17 | 14.524 | 0.019111 | 0 | 17 | 14.524 | 0.019111 | 0 | 17 | 0.019111
18 | 15.47 | 0.020355 | 0 | 0.012924 | 18 | 15.47 | 0.020355 | 0 | 18 | 15.47 | 0.020355 | 0 | 18 | 15.47 | 0.020355 | 0 | 18 | 0.020355
19 | 16.47 | 0.021671 | 0 | 0.013778 | 19 | 16.47 | 0.021671 | 0 | 19 | 16.47 | 0.021671 | 0 | 19 | 16.47 | 0.021671 | 0 | 19 | 0.021671
20 | 17.53 | 0.023066 | 0 | 0.014686 | 20 | 17.53 | 0.023066 | 0.023066 | 20 | 17.53 | 0.023066 | 0 | 20 | 17.53 | 0.023066 | 0 | 20 | 0.023066
21 | 18.64 | 0.024526 | 0 | 0.015639 | 21 | 18.64 | 0.024526 | 0 | 21 | 18.64 | 0.024526 | 0 | 21 | 18.64 | 0.024526 | 0 | 21 | 0.024526
22 | 19.82 | 0.026079 | 0 | 0.016655 | 22 | 19.82 | 0.026079 | 0 | 22 | 19.82 | 0.026079 | 0 | 22 | 19.82 | 0.026079 | 0 | 22 | 0.026079
23 | 21.06 | 0.027711 | 0 | 0.017727 | 23 | 21.06 | 0.027711 | 0 | 23 | 21.06 | 0.027711 | 0 | 23 | 21.06 | 0.027711 | 0 | 23 | 0.027711
24 | 22.37 | 0.029434 | 0 | 0.018863 | 24 | 22.37 | 0.029434 | 0 | 24 | 22.37 | 0.029434 | 0 | 24 | 22.37 | 0.029434 | 0 | 24 | 0.029434
25 | 23.75 | 0.03125 | 0 | 0.020065 | 25 | 23.75 | 0.03125 | 0 | 25 | 23.75 | 0.03125 | 0 | 25 | 23.75 | 0.03125 | 0 | 25 | 0.03125
26 | 25.2 | 0.033158 | 0 | 0.021332 | 26 | 25.2 | 0.033158 | 0 | 26 | 25.2 | 0.033158 | 0 | 26 | 25.2 | 0.033158 | 0 | 26 | 0.033158
27 | 26.37 | 0.034697 | 0 | 0.022358 | 27 | 26.37 | 0.034697 | 0 | 27 | 26.37 | 0.034697 | 0 | 27 | 26.37 | 0.034697 | 0 | 27 | 0.034697
28 | 28.34 | 0.037289 | 0 | 0.024092 | 28 | 28.34 | 0.037289 | 0 | 28 | 28.34 | 0.037289 | 0.037769 | 28 | 28.34 | 0.037289 | 0 | 28 | 0.037289
29 | 30.03 | 0.039513 | 0 | 0.025588 | 29 | 30.03 | 0.039513 | 0 | 29 | 30.03 | 0.039513 | 0 | 29 | 30.03 | 0.039513 | 0 | 29 | 0.039513
30 | 31.81 | 0.041855 | 0 | 0.027171 | 30 | 31.81 | 0.041855 | 0 | 30 | 31.81 | 0.041855 | 0 | 30 | 31.81 | 0.041855 | 0 | 30 | 0.041855
31 | 33.69 | 0.044329 | 0 | 0.028852 | 31 | 33.69 | 0.044329 | 0 | 31 | 33.69 | 0.044329 | 0 | 31 | 33.69 | 0.044329 | 0 | 31 | 0.044329
32 | 35.65 | 0.046908 | 0 | 0.030613 | 32 | 35.65 | 0.046908 | 0 | 32 | 35.65 | 0.046908 | 0 | 32 | 35.65 | 0.046908 | 0 | 32 | 0.046908
33 | 37.72 | 0.049632 | 0 | 0.032483 | 33 | 37.72 | 0.049632 | 0 | 33 | 37.72 | 0.049632 | 0 | 33 | 37.72 | 0.049632 | 0 | 33 | 0.049632
34 | 39.89 | 0.052487 | 0 | 0.034455 | 34 | 39.89 | 0.052487 | 0 | 34 | 39.89 | 0.052487 | 0 | 34 | 39.89 | 0.052487 | 0 | 34 | 0.052487
35 | 42.17 | 0.055487 | 0.055487 | 0.03654 | 35 | 42.17 | 0.055487 | 0 | 35 | 42.17 | 0.055487 | 0 | 35 | 42.17 | 0.055487 | 0 | 35 | 0.055487
36 | 44.55 | 0.058618 | 0 | 0.038731 | 36 | 44.55 | 0.058618 | 0 | 36 | 44.55 | 0.058618 | 0 | 36 | 44.55 | 0.058618 | 0 | 36 | 0.058618
37 | 47.06 | 0.061921 | 0 | 0.041057 | 37 | 47.06 | 0.061921 | 0 | 37 | 47.06 | 0.061921 | 0 | 37 | 47.06 | 0.061921 | 0 | 37 | 0.061921
38 | 49.69 | 0.065382 | 0 | 0.043512 | 38 | 49.69 | 0.065382 | 0 | 38 | 49.69 | 0.065382 | 0 | 38 | 49.69 | 0.065382 | 0 | 38 | 0.065382
39 | 52.44 | 0.069 | 0 | 0.046099 | 39 | 52.44 | 0.069 | 0 | 39 | 52.44 | 0.069 | 0 | 39 | 52.44 | 0.069 | 0 | 39 | 0.069
40 | 55.32 | 0.072789 | 0 | 0.048829 | 40 | 55.32 | 0.072789 | 0 | 40 | 55.32 | 0.072789 | 0 | 40 | 55.32 | 0.072789 | 0.072789 | 40 | 0.072789
41 | 58.33 | 0.07675 | 0 | 0.051707 | 41 | 58.33 | 0.07675 | 0 | 41 | 58.33 | 0.07675 | 0 | 41 | 58.33 | 0.07675 | 0 | 41 | 0.07675
42 | 61.49 | 0.080908 | 0 | 0.054755 | 42 | 61.49 | 0.080908 | 0 | 42 | 61.49 | 0.080908 | 0 | 42 | 61.49 | 0.080908 | 0 | 42 | 0.080908
43 | 64.8 | 0.085263 | 0 | 0.057977 | 43 | 64.8 | 0.085263 | 0 | 43 | 64.8 | 0.085263 | 0 | 43 | 64.8 | 0.085263 | 0 | 43 | 0.085263
44 | 68.25 | 0.089803 | 0 | 0.061368 | 44 | 68.25 | 0.089803 | 0 | 44 | 68.25 | 0.089803 | 0 | 44 | 68.25 | 0.089803 | 0 | 44 | 0.089803
45 | 71.87 | 0.094566 | 0 | 0.064963 | 45 | 71.87 | 0.094566 | 0 | 45 | 71.87 | 0.094566 | 0 | 45 | 71.87 | 0.094566 | 0 | 45 | 0.094566
46 | 75.65 | 0.099539 | 0 | 0.068758 | 46 | 75.65 | 0.099539 | 0 | 46 | 75.65 | 0.099539 | 0 | 46 | 75.65 | 0.099539 | 0 | 46 | 0.099539
47 | 79.6 | 0.10474 | 0 | 0.072768 | 47 | 79.6 | 0.10474 | 0 | 47 | 79.6 | 0.10474 | 0 | 47 | 79.6 | 0.10474 | 0 | 47 | 0.10474
48 | 83.72 | 0.11016 | 0 | 0.077 | 48 | 83.72 | 0.11016 | 0 | 48 | 83.72 | 0.11016 | 0 | 48 | 83.72 | 0.11016 | 0 | 48 | 0.11016
49 | 88.03 | 0.11583 | 0 | 0.081484 | 49 | 88.03 | 0.11583 | 0 | 49 | 88.03 | 0.11583 | 0 | 49 | 88.03 | 0.11583 | 0 | 49 | 0.11583
50 | 92.52 | 0.12174 | 0 | 0.086216 | 50 | 92.52 | 0.12174 | 0 | 50 | 92.52 | 0.12174 | 0 | 50 | 92.52 | 0.12174 | 0 | 50 | 0.12174
52 | 102.11 | 0.13436 | 0 | 0.09654 | 52 | 102.11 | 0.13436 | 0 | 52 | 102.11 | 0.13436 | 0 | 52 | 102.11 | 0.13436 | 0 | 52 | 0.13436
54 | 112.53 | 0.14807 | 0 | 0.1081 | 54 | 112.53 | 0.14807 | 0 | 54 | 112.53 | 0.14807 | 0 | 54 | 112.53 | 0.14807 | 0 | 54 | 0.14807
56 | 123.83 | 0.16293 | 0 | 0.12107 | 56 | 123.83 | 0.16293 | 0 | 56 | 123.83 | 0.16293 | 0 | 56 | 123.83 | 0.16293 | 0 | 56 | 0.16293
58 | 136.11 | 0.17909 | 0 | 0.1357 | 58 | 136.11 | 0.17909 | 0 | 58 | 136.11 | 0.17909 | 0 | 58 | 136.11 | 0.17909 | 0 | 58 | 0.17909
60 | 149.39 | 0.19657 | 0 | 0.15218 | 60 | 149.39 | 0.19657 | 0 | 60 | 149.39 | 0.19657 | 0 | 60 | 149.39 | 0.19657 | 0 | 60 | 0.19657
62 | 163.8 | 0.21553 | 0 | 0.17089 | 62 | 163.8 | 0.21553 | 0 | 62 | 163.8 | 0.21553 | 0 | 62 | 163.8 | 0.21553 | 0 | 62 | 0.21553
64 | 179.3 | 0.23592 | 0 | 0.19205 | 64 | 179.3 | 0.23592 | 0 | 64 | 179.3 | 0.23592 | 0 | 64 | 179.3 | 0.23592 | 0 | 64 | 0.23592
66 | 196.1 | 0.25803 | 0 | 0.2163 | 66 | 196.1 | 0.25803 | 0 | 66 | 196.1 | 0.25803 | 0 | 66 | 196.1 | 0.25803 | 0 | 66 | 0.25803
68 | 214.2 | 0.28184 | 0 | 0.2441 | 68 | 214.2 | 0.28184 | 0 | 68 | 214.2 | 0.28184 | 0 | 68 | 214.2 | 0.28184 | 0 | 68 | 0.28184
70 | 233.7 | 0.3075 | 0 | 0.27619 | 70 | 233.7 | 0.3075 | 0 | 70 | 233.7 | 0.3075 | 0 | 70 | 233.7 | 0.3075 | 0 | 70 | 0.3075
72 | 254.7 | 0.33513 | 0 | 0.31352 | 72 | 254.7 | 0.33513 | 0 | 72 | 254.7 | 0.33513 | 0 | 72 | 254.7 | 0.33513 | 0 | 72 | 0.33513
74 | 277.2 | 0.36474 | 0 | 0.35712 | 74 | 277.2 | 0.36474 | 0 | 74 | 277.2 | 0.36474 | 0 | 74 | 277.2 | 0.36474 | 0 | 74 | 0.36474
76 | 301.4 | 0.39658 | 0 | 0.40879 | 76 | 301.4 | 0.39658 | 0 | 76 | 301.4 | 0.39658 | 0 | 76 | 301.4 | 0.39658 | 0 | 76 | 0.39658
78 | 327.4 | 0.43079 | 0 | 0.47074 | 78 | 327.4 | 0.43079 | 0 | 78 | 327.4 | 0.43079 | 0 | 78 | 327.4 | 0.43079 | 0 | 78 | 0.43079
80 | 355.2 | 0.46737 | 0 | 0.54579 | 80 | 355.2 | 0.46737 | 0 | 80 | 355.2 | 0.46737 | 0 | 80 | 355.2 | 0.46737 | 0 | 80 | 0.46737
82 | 385 | 0.50658 | 0 | 0.63859 | 82 | 385 | 0.50658 | 0 | 82 | 385 | 0.50658 | 0 | 82 | 385 | 0.50658 | 0 | 82 | 0.50658
84 | 416.9 | 0.54855 | 0 | 0.75579 | 84 | 416.9 | 0.54855 | 0 | 84 | 416.9 | 0.54855 | 0 | 84 | 416.9 | 0.54855 | 0 | 84 | 0.54855
86 | 450.8 | 0.59316 | 0 | 0.90685 | 86 | 450.8 | 0.59316 | 0 | 86 | 450.8 | 0.59316 | 0 | 86 | 450.8 | 0.59316 | 0 | 86 | 0.59316
88 | 487.2 | 0.64105 | 0 | 1.1108 | 88 | 487.2 | 0.64105 | 0 | 88 | 487.2 | 0.64105 | 0 | 88 | 487.2 | 0.64105 | 0 | 88 | 0.64105
90 | 525.9 | 0.69197 | 0 | 1.3973 | 90 | 525.9 | 0.69197 | 0 | 90 | 525.9 | 0.69197 | 0 | 90 | 525.9 | 0.69197 | 0 | 90 | 0.69197
92 | 567.1 | 0.74618 | 0 | 1.8286 | 92 | 567.1 | 0.74618 | 0 | 92 | 567.1 | 0.74618 | 0 | 92 | 567.1 | 0.74618 | 0 | 92 | 0.74618
94 | 611 | 0.80395 | 0 | 2.5506 | 94 | 611 | 0.80395 | 0 | 94 | 611 | 0.80395 | 0 | 94 | 611 | 0.80395 | 0 | 94 | 0.80395
96 | 657.8 | 0.86553 | 0 | 4.0034 | 96 | 657.8 | 0.86553 | 0 | 96 | 657.8 | 0.86553 | 0 | 96 | 657.8 | 0.86553 | 0 | 96 | 0.86553
98 | 707.3 | 0.93066 | 0 | 8.348 | 98 | 707.3 | 0.93066 | 0 | 98 | 707.3 | 0.93066 | 0 | 98 | 707.3 | 0.93066 | 0 | 98 | 0.93066
100 | 760 | 1 | 0 |  | 100 | 760 | 1 | 0 | 100 | 760 | 1 | 0 | 100 | 760 | 1 | 0 | 100 | 1
110 | 1074.6 | 1.4139 | 0 |  | 110 | 1074.6 | 1.4139 | 0 | 110 | 1074.6 | 1.4139 | 0 | 110 | 1074.6 | 1.4139 | 0 | 110 | 1.4139
120 | 1489.2 | 1.9595 | 0 |  | 120 | 1489.2 | 1.9595 | 0 | 120 | 1489.2 | 1.9595 | 0 | 120 | 1489.2 | 1.9595 | 0 | 120 | 1.9595
130 | 2026.1 | 2.6659 | 0 |  | 130 | 2026.1 | 2.6659 | 0 | 130 | 2026.1 | 2.6659 | 0 | 130 | 2026.1 | 2.6659 | 0 | 130 | 2.6659
140 | 2710.9 | 3.567 | 0 |  | 140 | 2710.9 | 3.567 | 0 | 140 | 2710.9 | 3.567 | 0 | 140 | 2710.9 | 3.567 | 0 | 140 | 3.567
150 | 3570.5 | 4.698 | 0 |  | 150 | 3570.5 | 4.698 | 0 | 150 | 3570.5 | 4.698 | 0 | 150 | 3570.5 | 4.698 | 0 | 150 | 4.698
160 | 4636 | 6.1 | 0 |  | 160 | 4636 | 6.1 | 0 | 160 | 4636 | 6.1 | 0 | 160 | 4636 | 6.1 | 0 | 160 | 6.1
170 | 5940.9 | 7.817 | 0 |  | 170 | 5940.9 | 7.817 | 0 | 170 | 5940.9 | 7.817 | 0 | 170 | 5940.9 | 7.817 | 0 | 170 | 7.817
180 | 7521 | 9.8961 | 0 |  | 180 | 7521 | 9.8961 | 0 | 180 | 7521 | 9.8961 | 0 | 180 | 7521 | 9.8961 | 0 | 180 | 9.8961
190 | 9415.6 | 12.3889 | 0 |  | 190 | 9415.6 | 12.3889 | 0 | 190 | 9415.6 | 12.3889 | 0 | 190 | 9415.6 | 12.3889 | 0 | 190 | 12.3889
200 | 11664.5 | 15.348 | 0 |  | 200 | 11664.5 | 15.348 | 0 | 200 | 11664.5 | 15.348 | 0 | 200 | 11664.5 | 15.348 | 0 | 200 | 15.348
|  |  | 0.055487 |  |  |  |  | 0.023066 |  |  |  | 0.037769 |  |  |  | 0.072789